## Index
India data centres: all report tables in one place
259 tables from Reports 1–12, the simulator and the key-numbers sheet. Click a title to jump to it. Tabs R1–R12 hold every table copied from the full research reports. The "Atlas R1-R9" tab keeps extra tables built from the atlas charts and calculators for Reports 1–9 (chart data, capex build-ups, state scores), and the Simulator and Key numbers tabs hold the atlas model inputs.
# | Report | Table ID | Title (click to open) | Rows | Columns | Source | Sheet | Data basis | How it is used in the atlas | What it is used to derive
1 | Report 1 · Types of data centre | R1-T01 | Data-centre types by ownership and business model | 6 | 7 | Report 1 (full research report) · 1. Types of Data Centre › 1.1 Deep analysis of the types: what exists, what dominates globally, and why | R1 | Mixed: sourced figures plus estimates | Ch 1 "Type explorer" cards (how it works, cost, strengths, users) and the Type finder rules. | Which business model fits a project size and workload.
2 | Report 1 · Types of data centre | R1-T02 | Uptime Tiers: redundancy, availability and downtime | 4 | 7 | Report 1 (full research report) · 1. Types of Data Centre › 1.1 Deep analysis of the types: what exists, what dominates globally, and why | R1 | Source-derived (reported, not re-verified) | Ch 1 "What a Tier buys you" downtime clock. | Downtime hours a year = (1 − availability) × 8,760 per Tier.
3 | Report 1 · Types of data centre | R1-T03 | Cooling approaches: density, efficiency and water | 5 | 6 | Report 1 (full research report) · 1. Types of Data Centre › 1.1 Deep analysis of the types: what exists, what dominates globally, and why | R1 | Mixed: sourced figures plus estimates | Ch 3 cooling comparison text; density limits used in the Rack inspector bands. | Practical rack-density ceiling per cooling method.
4 | Report 1 · Types of data centre | R1-T04 | Global market share and installed capacity by type (2024–2026) | 11 | 3 | Report 1 (full research report) · 1. Types of Data Centre › 1.1 Deep analysis of the types: what exists, what dominates globally, and why | R1 | Source-derived (reported, not re-verified) | Ch 1 headline numbers and "Who owns the world's capacity" chart; Key numbers. | Global growth and hyperscale share trend to set India in context.
5 | Report 1 · Types of data centre | R1-T05 | India vs global capacity | 7 | 4 | Report 1 (full research report) · 1. Types of Data Centre › 1.2 Indian perspective: which types to build, why, and how | R1 | Source-derived (reported, not re-verified) | Ch 1 and Overview context; Key numbers (India operational capacity, pipeline). | India's share of global capacity; range of Indian capacity estimates.
6 | Report 1 · Types of data centre | R1-T06 | Key Indian hubs (Cushman & Wakefield, H1 2026) | 8 | 4 | Report 1 (full research report) · 1. Types of Data Centre › 1.2 Indian perspective: which types to build, why, and how | R1 | Source-derived (reported, not re-verified) | Ch 1 "India by city" chart; Ch 9 map (live and pipeline MW); Ch 10 demand scores; Ch 11 starting point. | City shares, pipeline-to-stock ratios, forecast anchor (1,789 MW).
7 | Report 1 · Types of data centre | R1-T07 | State policies: key terms | 7 | 4 | Report 1 (full research report) · 1. Types of Data Centre › 1.2 Indian perspective: which types to build, why, and how | R1 | Source-derived (reported, not re-verified) | Superseded by Report 9 tables; feeds Ch 9 policy register. | Early comparison of state incentives.
8 | Report 2 · AI vs conventional | R2-T01 | Electricity split by subsystem and facility class | 4 | 5 | Report 2 (full research report) · Section 1: Anatomy of Data Centre Consumption › 1.1 Electricity breakdown by subsystem | R2 | Illustrative / framework / author judgement | Ch 2 "Where the power goes, by facility class" chart. | Overhead share of energy by facility class; PUE build-up.
9 | Report 2 · AI vs conventional | R2-T02 | Server power split: conventional CPU vs AI accelerated | 5 | 3 | Report 2 (full research report) · Section 1: Anatomy of Data Centre Consumption › 1.2 Inside the IT load: CPUs, GPUs, memory, storage and networking | R2 | Illustrative / framework / author judgement | Ch 2 text on IT-load anatomy (reference). | Share of rack power going to accelerators.
10 | Report 2 · AI vs conventional | R2-T03 | Efficiency metrics: PUE, WUE, CUE and ERE | 4 | 3 | Report 2 (full research report) · Section 1: Anatomy of Data Centre Consumption › 1.3 Efficiency metrics: PUE, WUE, CUE and ERE | R2 | Source-derived (reported, not re-verified) | Ch 2 and Ch 8 metric definitions; Key numbers (PUE 1.54, Google 1.09, MeitY <1.35). | PUE and WUE benchmarks for calculators.
11 | Report 2 · AI vs conventional | R2-T04 | Water per AI query: a contested range | 4 | 3 | Report 2 (full research report) · Section 1: Anatomy of Data Centre Consumption › 1.4 Water consumption: direct and indirect | R2 | Source-derived (reported, not re-verified) | Ch 6 and Ch 12 "Water per AI prompt" charts. | Water per prompt with different boundaries.
12 | Report 2 · AI vs conventional | R2-T05 | US data-centre electricity (LBNL 2024) | 4 | 3 | Report 2 (full research report) · Section 1: Anatomy of Data Centre Consumption › 1.6 Global and regional electricity consumption | R2 | Source-derived (reported, not re-verified) | Ch 2 context text (reference only). | US growth path as a comparison for India.
13 | Report 2 · AI vs conventional | R2-T06 | Energy per workload | 6 | 3 | Report 2 (full research report) · Section 1: Anatomy of Data Centre Consumption › 1.7 Energy per workload | R2 | Source-derived (reported, not re-verified) | Ch 2 "Energy per workload" table. | Energy per query/training run; continuous MW for inference.
14 | Report 2 · AI vs conventional | R2-T07 | Master comparison: AI vs conventional data centres | 15 | 3 | Report 2 (full research report) · Section 2: AI Data Centre vs Conventional Data Centre › 2.1 Master comparison table | R2 | Mixed: sourced figures plus estimates | Ch 2 "Conventional vs AI" comparison table. | Design differences that drive cooling, power and capex choices.
15 | Report 2 · AI vs conventional | R2-T08 | Compute hardware and power | 8 | 3 | Report 2 (full research report) · Section 2: AI Data Centre vs Conventional Data Centre › 2.3 Compute hardware and power | R2 | Mixed: sourced figures plus estimates | Ch 2 "Rack density and chip power" chart and Rack inspector. | kW per rack and per GPU used in sizing.
16 | Report 2 · AI vs conventional | R2-T09 | Training vs inference data centres | 6 | 3 | Report 2 (full research report) · Section 2: AI Data Centre vs Conventional Data Centre › 2.15 Inference versus training data centres | R2 | Illustrative / framework / author judgement | Ch 2 "Training vs inference sites" table. | Siting rule: train near power, serve inference near users.
17 | Report 3 · Cooling | R3-T01 | Accelerator power trend per GPU | 6 | 4 | Report 3 (full research report) · 1. Fundamentals › 1.1 Why cooling is needed | R3 | Mixed: sourced figures plus estimates | Ch 3 cooling chain and GPU power figures. | Why air cooling stops working as GPUs pass ~1 kW.
18 | Report 3 · Cooling | R3-T02 | Heat transfer properties of cooling fluids | 5 | 6 | Report 3 (full research report) · 1. Fundamentals › 1.2 Heat transfer properties: why liquid wins | R3 | Source-derived (reported, not re-verified) | Ch 3 "Why liquid wins" chart. | Flow needed to move heat with air vs water.
19 | Report 3 · Cooling | R3-T03 | ASHRAE air-cooled classes (IT inlet air) | 5 | 4 | Report 3 (full research report) · 1. Fundamentals › 1.3 ASHRAE TC 9.9 thermal guidelines (5th edition, 2021) | R3 | Source-derived (reported, not re-verified) | Ch 3 reference (ASHRAE classes). | Allowable inlet temperatures; economiser hours.
20 | Report 3 · Cooling | R3-T04 | ASHRAE liquid-cooling W classes | 6 | 3 | Report 3 (full research report) · 1. Fundamentals › 1.3 ASHRAE TC 9.9 thermal guidelines (5th edition, 2021) | R3 | Source-derived (reported, not re-verified) | Ch 3 "Warm-water explorer" (W32–W45 setpoints). | Which heat rejection works at a given facility water temperature.
21 | Report 3 · Cooling | R3-T05 | Key cooling metrics | 8 | 3 | Report 3 (full research report) · 1. Fundamentals › 1.5 Key metrics | R3 | Mixed: sourced figures plus estimates | Ch 3 and simulator PUE/WUE reasoning (reference). | Typical PUE/WUE ranges for calculators.
22 | Report 3 · Cooling | R3-T06 | Chiller types | 6 | 5 | Report 3 (full research report) · 3. Chilled-water plants and heat rejection › 3.1 Chiller types | R3 | Mixed: sourced figures plus estimates | Reference only (chiller choice in Ch 3 text). | Chiller efficiency assumptions.
23 | Report 3 · Cooling | R3-T07 | Liquid cooling comparison | 10 | 6 | Report 3 (full research report) · 4. Liquid cooling types › 4.7 Liquid cooling comparison | R3 | Mixed: sourced figures plus estimates | Ch 3 "Liquid cooling compared" table. | Density, PUE and maturity per liquid technology.
24 | Report 3 · Cooling | R3-T08 | Natural and alternative cooling | 6 | 4 | Report 3 (full research report) · 5. Natural and alternative cooling | R3 | Mixed: sourced figures plus estimates | Ch 3 text on natural cooling; Ch 12 seawater option. | Relevance of seawater and free cooling for India.
25 | Report 3 · Cooling | R3-T09 | Liquid-cooling market size and forecasts | 6 | 3 | Report 3 (full research report) · 6. Market and adoption › 6.1 Market size and forecasts (2024–2031) | R3 | Source-derived (reported, not re-verified) | Ch 3 "Liquid-cooling market" chart; Ch 11 Bass diffusion analogue. | Adoption speed for liquid cooling.
26 | Report 3 · Cooling | R3-T10 | Cooling vendor landscape and consolidation | 8 | 2 | Report 3 (full research report) · 6. Market and adoption › 6.4 Vendor landscape and consolidation (2024–2026) | R3 | Source-derived (reported, not re-verified) | Ch 3 "Who bought whom" bars. | Supply-chain concentration risk.
27 | Report 3 · Cooling | R3-T11 | Water–energy trade-off by heat-rejection type | 7 | 4 | Report 3 (full research report) · 7. Water–energy trade-offs › 7.1 The core trade | R3 | Mixed: sourced figures plus estimates | Ch 3 heat-rejection table; simulator WUE functions; Ch 12 power-vs-water chart. | Water vs energy trade-off per design.
28 | Report 3 · Cooling | R3-T12 | Cooling capex by approach (indicative) | 5 | 3 | Report 3 (full research report) · 8. Cost › 8.1 Capex by cooling approach (indicative, 2025–26) | R3 | Proxy / estimate | Simulator cooling capex adder (₹0–3 cr/MW). | Capex premium for liquid cooling.
29 | Report 3 · Cooling | R3-T13 | Indian city climates and free-cooling outlook | 6 | 4 | Report 3 (full research report) · 9. The Indian perspective › 9.1 Climate challenge | R3 | Proxy / estimate | Ch 3 city cards; simulator design temperatures; Ch 4 day model. | Free-cooling potential and PUE by city.
30 | Report 3 · Cooling | R3-T14 | Indian operators: liquid-cooling deployments | 7 | 2 | Report 3 (full research report) · 9. The Indian perspective › 9.2 Indian operators and liquid cooling deployments | R3 | Source-derived (reported, not re-verified) | Ch 3 "Indian deployments" list. | State of liquid cooling in India.
31 | Report 3 · Cooling | R3-T15 | Recommended cooling for India by use case | 7 | 4 | Report 3 (full research report) · 9. The Indian perspective › 9.6 Recommendations for India: what to use where | R3 | Illustrative / framework / author judgement | Ch 3 "What to use where in India" table. | Recommended design per use case and city.
32 | Report 4 · Bengaluru water and power | R4-T01 | Assumptions for the three Bengaluru cases | 8 | 4 | Report 4 (full research report) · 1. Assumptions | R4 | Proxy / estimate | Ch 4 campus calculator presets; simulator defaults. | Input assumptions for the three Bengaluru cases.
33 | Report 4 · Bengaluru water and power | R4-T02 | Power calculations by case | 14 | 4 | Report 4 (full research report) · 2. Power calculations | R4 | Calculated (model output) | Ch 4 calculator outputs (MU, MVA, homes, % of state demand); Key numbers (841 MU, 140 MVA). | Energy, contract demand and share of Karnataka demand per case.
34 | Report 4 · Bengaluru water and power | R4-T03 | On-site water by case | 6 | 6 | Report 4 (full research report) · 3. Water calculations › 3.2 On-site water by case | R4 | Calculated (model output) | Ch 4 water bars and "Water you can picture" (Ch 6). | On-site MLD and people-equivalent per case.
35 | Report 4 · Bengaluru water and power | R4-T04 | Indirect water embedded in grid electricity | 3 | 4 | Report 4 (full research report) · 3. Water calculations › 3.3 Indirect water embedded in grid electricity | R4 | Calculated (model output) | Ch 4 power-station water bar; simulator grid water (KA 1.5 L/kWh). | Indirect water per case.
36 | Report 4 · Bengaluru water and power | R4-T05 | Comparison with other Bengaluru and Karnataka water users | 18 | 5 | Report 4 (full research report) · 4. Comparison with other Bengaluru and Karnataka users | R4 | Mixed: sourced figures plus estimates | Ch 4 "Compared with other users" chart. | Data-centre water in context of other users.
37 | Report 4 · Bengaluru water and power | R4-T06 | Where Bengaluru data centres get water today | 5 | 3 | Report 4 (full research report) · 5. Where Bengaluru data centres get water today | R4 | Source-derived (reported, not re-verified) | Ch 4 "The city's water" table. | Sources and prices of water in Bengaluru.
38 | Report 4 · Bengaluru water and power | R4-T07 | Scenarios: added IT capacity vs water (75% utilisation) | 5 | 5 | Report 4 (full research report) · 6. Will data centre water cause scarcity? › 6.2 Scenarios (75% utilisation; IT energy = 18,000 kWh/day per MW) | R4 | Calculated (model output) | Ch 4 "Scaling to 1 GW" chart; Key numbers (~32 MLD). | City-wide water impact of the 1 GW target.
39 | Report 4 · Bengaluru water and power | R4-T08 | Phased roadmap for Karnataka | 3 | 3 | Report 4 (full research report) · Recommendations › Phased roadmap | R4 | Illustrative / framework / author judgement | Ch 4 "Recommended roadmap" table. | Policy sequence for Karnataka.
40 | Report 5 · Carbon | R5-T01 | Lifecycle carbon intensity by technology | 10 | 5 | Report 5 (full research report) · 1. SOURCE — What Generates the Electron › 1.1 Lifecycle carbon intensity by technology | R5 | Source-derived (reported, not re-verified) | Ch 5 "Lifecycle carbon by source" bars. | Carbon of procurement options.
41 | Report 5 · Carbon | R5-T02 | Water withdrawal vs consumption by generation source | 12 | 4 | Report 5 (full research report) · 1. SOURCE — What Generates the Electron › 1.2 Water: withdrawal vs consumption by source | R5 | Mixed: sourced figures plus estimates | Ch 5 "Water consumed by source" bars; grid water in calculators. | Indirect water per kWh by source.
42 | Report 5 · Carbon | R5-T03 | Country grid carbon intensity | 8 | 4 | Report 5 (full research report) · 3. LOCATION — Which Grid, Which Margin, Which Basin › 3.1 Country grids (operational, annual average) | R5 | Mixed: sourced figures plus estimates | Ch 5 "1 TWh, seven ways" chart. | Carbon of the same TWh on different grids.
43 | Report 5 · Carbon | R5-T04 | India emission-factor types: average vs marginal | 5 | 3 | Report 5 (full research report) · 3. LOCATION — Which Grid, Which Margin, Which Basin › 3.3 Average vs marginal; attributional vs consequential | R5 | Mixed: sourced figures plus estimates | Ch 5 text on average vs marginal factors. | Which factor to use for reporting vs siting.
44 | Report 5 · Carbon | R5-T05 | Hyperscaler Scope 2: location-based vs market-based | 3 | 5 | Report 5 (full research report) · 4. CARBON INTENSITY — Definitions, Trajectory and Data-Centre Metrics › 4.4 Hyperscaler disclosures: location-based vs market-based | R5 | Source-derived (reported, not re-verified) | Ch 5 Microsoft Scope 2 chart. | Gap between location- and market-based claims.
45 | Report 5 · Carbon | R5-T06 | Grid-average water intensity | 6 | 3 | Report 5 (full research report) · 5. WATER INTENSITY — The Grid's Hidden Water › 5.2 Grid-average water intensity | R5 | Mixed: sourced figures plus estimates | Grid water intensity used in Ch 4–6 and simulator (1.5–2.2 L/kWh). | Indirect water per kWh.
46 | Report 5 · Carbon | R5-T07 | Worked matrix: carbon and water per TWh by scenario | 12 | 8 | Report 5 (full research report) · SYNTHESIS — "Every TWh Is Not the Same": Worked Matrix | R5 | Calculated (model output) | Ch 5 "1 TWh of data-centre load, seven ways" chart (carbon and water). | Carbon and water per TWh by supply scenario.
47 | Report 5 · Carbon | R5-T08 | Five-factor scorecard | 6 | 7 | Report 5 (full research report) · SYNTHESIS — "Every TWh Is Not the Same": Worked Matrix › Five-factor scorecard (for a site or procurement decision) | R5 | Illustrative / framework / author judgement | Ch 5 five-factor scorecard calculator. | Weighted score for a site or power contract.
48 | Report 6 · Water impact | R6-T01 | Withdrawal vs consumption: definitions by framework | 4 | 4 | Report 6 (full research report) · 1. How much water? › 1.1 Withdrawal vs consumption: definitions and why both matter | R6 | Source-derived (reported, not re-verified) | Ch 6 framing (reference). | Separate withdrawal, consumption, discharge.
49 | Report 6 · Water impact | R6-T02 | Cooling water by system | 6 | 4 | Report 6 (full research report) · 1. How much water? › 1.2 Cooling water | R6 | Mixed: sourced figures plus estimates | Ch 6 water balance and simulator WUE values. | Site WUE by cooling system.
50 | Report 6 · Water impact | R6-T03 | Non-cooling water uses (50 MW campus) | 8 | 3 | Report 6 (full research report) · 1. How much water? › 1.3 Non-cooling water | R6 | Proxy / estimate | Ch 6 water balance (non-cooling 14.6 ML/yr). | Non-cooling water allowance.
51 | Report 6 · Water impact | R6-T04 | Freshwater vs recycled water sources (Bengaluru) | 5 | 4 | Report 6 (full research report) · 1. How much water? › 1.4 Freshwater vs recycled water | R6 | Mixed: sourced figures plus estimates | Ch 6 water balance source options; simulator water sources. | Source choice and cycles of concentration.
52 | Report 6 · Water impact | R6-T05 | Daily and annual water demand by capacity and cooling | 4 | 5 | Report 6 (full research report) · 1. How much water? › 1.5 Daily and annual demand: worked examples | R6 | Calculated (model output) | Ch 6 and Ch 12 reference values. | Daily and annual water per MW and design.
53 | Report 6 · Water impact | R6-T06 | Water balance: 50 MW evaporative facility at different CoC | 12 | 6 | Report 6 (full research report) · 2. Water balance › 2.3 Worked balance: 50 MW Bengaluru hyperscale facility (evaporative) | R6 | Calculated (model output) | Ch 6 "Cooling-tower water balance" calculator. | Withdrawal, consumption, discharge at each CoC.
54 | Report 6 · Water impact | R6-T07 | Water balance: 100 MW AI facility (DLC + adiabatic) | 9 | 3 | Report 6 (full research report) · 2. Water balance › 2.4 Worked balance: 100 MW AI facility (DLC + adiabatic dry coolers) | R6 | Calculated (model output) | Ch 6 text; Ch 12 Example C reasoning. | DLC water and peak factor (3.5×).
55 | Report 6 · Water impact | R6-T08 | Water measurement and accounting standards | 8 | 3 | Report 6 (full research report) · 2. Water balance › 2.5 Measurement and accounting standards | R6 | Source-derived (reported, not re-verified) | Reference only (metering and standards). | Disclosure design.
56 | Report 6 · Water impact | R6-T09 | Water per MW of IT capacity | 5 | 4 | Report 6 (full research report) · 3. Water intensity metrics › 3.2 L/MW (per MW of IT capacity) | R6 | Calculated (model output) | Reference only (per-MW benchmark). | Water per MW for allocations.
57 | Report 6 · Water impact | R6-T10 | Water per GPU-hour | 3 | 5 | Report 6 (full research report) · 3. Water intensity metrics › 3.4 L/GPU-hour | R6 | Calculated (model output) | Ch 6 text (water per GPU-hour). | Water per GPU-hour.
58 | Report 6 · Water impact | R6-T11 | Water per inference and training | 6 | 3 | Report 6 (full research report) · 3. Water intensity metrics › 3.5 L/inference and training | R6 | Mixed: sourced figures plus estimates | Ch 6 "Water per AI prompt" chart. | Per-prompt water by boundary.
59 | Report 6 · Water impact | R6-T12 | Which water metric for which audience | 5 | 2 | Report 6 (full research report) · 3. Water intensity metrics › 3.6 Which metric for which audience, pitfalls and normalisation | R6 | Illustrative / framework / author judgement | Reference only. | Which metric for regulator, customer, citizen.
60 | Report 6 · Water impact | R6-T13 | Bengaluru scenarios compared (S1–S4) | 10 | 5 | Report 6 (full research report) · 3. Water intensity metrics › 3.7 Single comparison table: Bengaluru scenarios | R6 | Calculated (model output) | Ch 6 Bengaluru scenario table. | Site vs source WUE for S1–S4.
61 | Report 6 · Water impact | R6-T14 | Bengaluru sector water-use estimates | 5 | 3 | Report 6 (full research report) · 4. Local context › 4.1 Data centre use against Bengaluru's water availability | R6 | Source-derived (reported, not re-verified) | Ch 4 "How much do Bengaluru's data centres use today?" chart. | Range of sector water estimates.
62 | Report 6 · Water impact | R6-T15 | Equivalence metrics (S2, 50 MW evaporative) | 8 | 2 | Report 6 (full research report) · 4. Local context › 4.3 Equivalence metrics (S2, 50 MW evaporative) | R6 | Calculated (model output) | Ch 6 "Water you can picture" (people, tankers, pools). | Everyday equivalents of site water.
63 | Report 6 · Water impact | R6-T16 | Water-stress frameworks | 5 | 4 | Report 6 (full research report) · 5. Water stress › 5.1 Frameworks | R6 | Source-derived (reported, not re-verified) | Reference only (water-stress frameworks). | Choice of scarcity method.
64 | Report 6 · Water impact | R6-T17 | Proposed materiality thresholds | 4 | 4 | Report 6 (full research report) · 5. Water stress › 5.2 Methods | R6 | Illustrative / framework / author judgement | Ch 6 thresholds logic (reference). | Materiality tests for permits.
65 | Report 6 · Water impact | R6-T18 | Scarcity-weighted footprint by scenario (50 MW) | 6 | 8 | Report 6 (full research report) · 5. Water stress › 5.3 Applying the methods to Bengaluru scenarios (50 MW, annual) | R6 | Calculated (model output) | Ch 6 "Scarcity-weighted water footprint" chart. | Footprint ranking of design and source options.
66 | Report 6 · Water impact | R6-T19 | Water impact scorecard | 7 | 7 | Report 6 (full research report) · 5. Water stress › 5.4 Water impact scorecard | R6 | Illustrative / framework / author judgement | Ch 6 "Impact scorecard" table. | Refuse / redesign / acceptable decision per scenario.
67 | Report 6 · Water impact | R6-T20 | Hyperscaler water reporting: practices and gaps | 4 | 3 | Report 6 (full research report) · Hyperscaler and Indian operator water reporting: practices and gaps | R6 | Source-derived (reported, not re-verified) | Ch 6 disclosure text; Ch 12 fleet dots. | Benchmark WUE values of operators.
68 | Report 6 · Water impact | R6-T21 | Minimum water disclosure framework | 8 | 4 | Report 6 (full research report) · Recommendations › A. Minimum measurement and disclosure framework (all sites ≥500 kW IT) | R6 | Illustrative / framework / author judgement | Ch 6 "Seven metrics every site should publish". | Minimum disclosure standard.
69 | Report 6 · Water impact | R6-T22 | Suggested water thresholds | 6 | 4 | Report 6 (full research report) · Recommendations › C. Suggested thresholds | R6 | Illustrative / framework / author judgement | Ch 6 "Suggested thresholds" table. | Green/amber/red ratings.
70 | Report 7 · Unit economics | R7-T01 | Construction cost index by market (Turner & Townsend) | 12 | 4 | Report 7 (full research report) · 1. CAPEX (₹) › 1.1 Global and Indian benchmarks | R7 | Source-derived (reported, not re-verified) | Ch 7 "Build cost around the world" chart; Key numbers. | Mumbai cost advantage; forecast base cost.
71 | Report 7 · Unit economics | R7-T02 | Land prices in Indian data-centre hubs | 8 | 3 | Report 7 (full research report) · 1. CAPEX (₹) › 1.2 Land and buildings | R7 | Mixed: sourced figures plus estimates | Ch 7 "Land and power" table; simulator land prices. | Land share of capex by hub.
72 | Report 7 · Unit economics | R7-T03 | Servers, storage and GPU prices | 8 | 4 | Report 7 (full research report) · 1. CAPEX (₹) › 1.3 Servers, storage and GPUs (IT capex) | R7 | Mixed: sourced figures plus estimates | Ch 7 GPU calculator (HGX prices); simulator GPU capex. | IT capex per MW and per GPU.
73 | Report 7 · Unit economics | R7-T04 | Soft costs, interest during construction and contingency | 3 | 3 | Report 7 (full research report) · 1. CAPEX (₹) › 1.8 Soft costs, interest during construction and contingency | R7 | Proxy / estimate | Capex stacks (soft costs, contingency, IDC). | Soft-cost share of capex.
74 | Report 7 · Unit economics | R7-T05 | Capex breakdown: 20 MW Tier III colocation | 13 | 4 | Report 7 (full research report) · 1. CAPEX (₹) › 1.9 Breakdown tables for the three cases | R7 | Calculated (model output) | Ch 7 "Line by line" table (Case A) and capex chart; simulator colo capex ₹56.1 cr/MW. | Capex per MW for a colo.
75 | Report 7 · Unit economics | R7-T06 | Capex breakdown: 50 MW hyperscale build-to-suit | 13 | 4 | Report 7 (full research report) · 1. CAPEX (₹) › 1.9 Breakdown tables for the three cases | R7 | Calculated (model output) | Ch 7 "Line by line" (Case B); simulator hyperscale ₹39.2 cr/MW. | Capex per MW for hyperscale.
76 | Report 7 · Unit economics | R7-T07 | Capex breakdown: 100 MW AI campus incl. GPUs | 14 | 4 | Report 7 (full research report) · 1. CAPEX (₹) › 1.9 Breakdown tables for the three cases | R7 | Calculated (model output) | Ch 7 "Line by line" (Case C); simulator AI ₹72.5 + ₹266 cr/MW. | Capex per MW for an AI campus incl. GPUs.
77 | Report 7 · Unit economics | R7-T08 | State HT/EHT tariffs for data centres (FY2025–26) | 5 | 5 | Report 7 (full research report) · 2. OPEX (₹) › 2.1 Electricity | R7 | Mixed: sourced figures plus estimates | Simulator tariffs (KA, MH, TN, TG); Ch 7 land and power table. | Power bill and LCOD.
78 | Report 7 · Unit economics | R7-T09 | Annual electricity cost by tariff and case | 5 | 5 | Report 7 (full research report) · 2. OPEX (₹) › 2.1 Electricity | R7 | Calculated (model output) | Reference for simulator power bill. | Annual electricity cost by state.
79 | Report 7 · Unit economics | R7-T10 | Water bill by case | 3 | 5 | Report 7 (full research report) · 2. OPEX (₹) › 2.2 Water | R7 | Calculated (model output) | Simulator water cost line. | Water cost share of opex (<2%).
80 | Report 7 · Unit economics | R7-T11 | Indian salary markers | 5 | 3 | Report 7 (full research report) · 2. OPEX (₹) › 2.5 Personnel | R7 | Source-derived (reported, not re-verified) | Reference only (personnel cost basis). | Staff cost per FTE.
81 | Report 7 · Unit economics | R7-T12 | Opex: Case A, 20 MW colocation | 12 | 2 | Report 7 (full research report) · 2. OPEX (₹) › 2.8 Opex tables per case (stabilised year) | R7 | Calculated (model output) | Ch 7 "Where colo opex goes" chart; LCOD calculator. | Opex per MW, power share.
82 | Report 7 · Unit economics | R7-T13 | Opex: Case B, 50 MW hyperscale | 12 | 2 | Report 7 (full research report) · 2. OPEX (₹) › 2.8 Opex tables per case (stabilised year) | R7 | Calculated (model output) | Reference (hyperscale opex in LCOD preset B). | Opex per MW for hyperscale.
83 | Report 7 · Unit economics | R7-T14 | Opex: Case C, 100 MW AI campus | 12 | 2 | Report 7 (full research report) · 2. OPEX (₹) › 2.8 Opex tables per case (stabilised year) | R7 | Calculated (model output) | Reference (AI preset C in LCOD). | Opex per MW for AI campus.
84 | Report 7 · Unit economics | R7-T15 | Colocation pricing in India | 7 | 3 | Report 7 (full research report) · 3. Unit economics › 3.1 ₹ per MW: capex, revenue, EBITDA, payback, IRR, valuation | R7 | Source-derived (reported, not re-verified) | Simulator break-even rent comparison; Ch 7 text; Key numbers. | Market rent vs break-even.
85 | Report 7 · Unit economics | R7-T16 | Per-MW economics by case | 10 | 4 | Report 7 (full research report) · 3. Unit economics › 3.1 ₹ per MW: capex, revenue, EBITDA, payback, IRR, valuation | R7 | Calculated (model output) | Ch 7 "Returns by business model" table. | EBITDA, payback, IRR per model.
86 | Report 7 · Unit economics | R7-T17 | Valuations (EV/MW and EV/EBITDA) | 4 | 2 | Report 7 (full research report) · 3. Unit economics › 3.1 ₹ per MW: capex, revenue, EBITDA, payback, IRR, valuation | R7 | Source-derived (reported, not re-verified) | Ch 7 text (Nxtra valuation). | Value per MW vs replacement cost.
87 | Report 7 · Unit economics | R7-T18 | Cost per rack by density | 4 | 6 | Report 7 (full research report) · 3. Unit economics › 3.2 ₹ per rack | R7 | Calculated (model output) | Reference only (cost per rack). | Capex and rent per rack by density.
88 | Report 7 · Unit economics | R7-T19 | Levelised cost of data-centre capacity (LCOD) | 4 | 7 | Report 7 (full research report) · 3. Unit economics › 3.3 ₹ per kWh: levelised cost of data centre capacity (LCOD) | R7 | Calculated (model output) | Ch 7 LCOD calculator (CRF method); simulator cost per IT-kWh. | Levelised cost per IT-kWh.
89 | Report 7 · Unit economics | R7-T20 | Cost per GPU-hour by utilisation | 4 | 6 | Report 7 (full research report) · 3. Unit economics › 3.4 Cost per GPU-hour: TCO in India vs market prices | R7 | Calculated (model output) | Ch 7 GPU-hour calculator and chart. | GPU-hour cost at each utilisation.
90 | Report 7 · Unit economics | R7-T21 | GPU-hour market prices and break-even utilisation | 9 | 3 | Report 7 (full research report) · 3. Unit economics › 3.4 Cost per GPU-hour: TCO in India vs market prices | R7 | Source-derived (reported, not re-verified) | Ch 7 market-price table and dashed lines on GPU chart. | Break-even utilisation vs market prices.
91 | Report 7 · Unit economics | R7-T22 | Sensitivity analysis | 7 | 4 | Report 7 (full research report) · 3. Unit economics › 3.5 Sensitivity analysis | R7 | Calculated (model output) | Ch 7 "What moves the colo's cost" tornado chart. | Which lever matters most.
92 | Report 7 · Unit economics | R7-T23 | India vs US vs Singapore | 7 | 4 | Report 7 (full research report) · 3. Unit economics › 3.6 Comparing models and markets | R7 | Source-derived (reported, not re-verified) | Ch 7 "India vs US vs Singapore" table. | India's thin margin vs peers.
93 | Report 7 · Unit economics | R7-T24 | Colocation vs hyperscale vs AI neocloud | 5 | 4 | Report 7 (full research report) · 3. Unit economics › 3.6 Comparing models and markets | R7 | Calculated (model output) | Ch 7 returns comparison text. | Business-model risk profile.
94 | Report 8 · Green data centres | R8-T01 | Twelve dimensions of a green data centre | 12 | 5 | Report 8 (full research report) · 1. What is a "green data centre"? › 1.2 The twelve dimensions | R8 | Illustrative / framework / author judgement | Ch 8 "Twelve dimensions" grid. | Definition of green for India.
95 | Report 8 · Green data centres | R8-T02 | Green vs greenwashing: a quick test | 5 | 3 | Report 8 (full research report) · 1. What is a "green data centre"? › 1.3 Green vs greenwashing: a quick test | R8 | Illustrative / framework / author judgement | Ch 8 "Spotting greenwashing" table. | Credibility test for claims.
96 | Report 8 · Green data centres | R8-T03 | Core green metrics and formulas | 9 | 4 | Report 8 (full research report) · 2. Metrics and standards › 2.1 Core metrics and formulas | R8 | Source-derived (reported, not re-verified) | Ch 8 metric definitions (reference). | CUE, ERF, CFE formulas.
97 | Report 8 · Green data centres | R8-T04 | Certifications compared | 8 | 4 | Report 8 (full research report) · 2. Metrics and standards › 2.3 Certifications | R8 | Source-derived (reported, not re-verified) | Reference only (certifications). | Which label to pursue.
98 | Report 8 · Green data centres | R8-T05 | Indian standards and policy instruments | 9 | 3 | Report 8 (full research report) · 2. Metrics and standards › 2.4 Indian standards and policy instruments | R8 | Source-derived (reported, not re-verified) | Ch 8 "Rules elsewhere" (India row) and Ch 9 central framework. | Indian policy instruments status.
99 | Report 8 · Green data centres | R8-T06 | Design levers with quantified savings | 17 | 4 | Report 8 (full research report) · 3. Design levers with quantified savings | R8 | Proxy / estimate | Reference for green upgrade assumptions. | Savings per design lever.
100 | Report 8 · Green data centres | R8-T07 | Renewable procurement options in India | 10 | 5 | Report 8 (full research report) · 4. Renewable and carbon-free energy procurement › 4.1 Procurement options in India | R8 | Mixed: sourced figures plus estimates | Ch 8 "Buying clean power in India" table; simulator RE price. | Landed cost of clean power routes.
101 | Report 8 · Green data centres | R8-T08 | Indian operator green snapshot | 8 | 3 | Report 8 (full research report) · 4. Renewable and carbon-free energy procurement › 4.4 Indian operator snapshot | R8 | Source-derived (reported, not re-verified) | Ch 8 "Indian operators" table. | Operator green credentials.
102 | Report 8 · Green data centres | R8-T09 | Global benchmarks: Google, Microsoft and others | 3 | 5 | Report 8 (full research report) · 5. Global benchmarks and the AI problem | R8 | Source-derived (reported, not re-verified) | Ch 8 headline (+18% / +25% emissions); Ch 5 text. | Limits of annual RE matching.
103 | Report 8 · Green data centres | R8-T10 | Green upgrade worked example: assumptions | 12 | 4 | Report 8 (full research report) · 6. Economics of going green: a 20 MW Bengaluru colocation worked example › 6.1 Assumptions (flagged estimates) | R8 | Proxy / estimate | Ch 8 green upgrade calculator defaults. | Inputs for the 20 MW green case.
104 | Report 8 · Green data centres | R8-T11 | Marginal abatement cost by package | 4 | 4 | Report 8 (full research report) · 6. Economics of going green: a 20 MW Bengaluru colocation worked example › 6.3 Marginal abatement cost (MAC) | R8 | Calculated (model output) | Ch 8 "Abatement cost by measure" chart; Key numbers. | Marginal abatement cost per package.
105 | Report 8 · Green data centres | R8-T12 | Green data-centre maturity model (India-calibrated) | 8 | 6 | Report 8 (full research report) · 8. Green Data Centre maturity model (India-calibrated) | R8 | Illustrative / framework / author judgement | Ch 8 maturity self-check radar. | Maturity level per dimension.
106 | Report 9 · State policies | R9-T01 | Central framework instruments | 12 | 3 | Report 9 (full research report) · Part A — Central Framework | R9 | Source-derived (reported, not re-verified) | Ch 9 "The central framework" table. | National levers vs state levers.
107 | Report 9 · State policies | R9-T02 | Telangana named projects | 5 | 3 | Report 9 (full research report) · Part B — State-by-State Deep Dive › 4. Telangana — the inland AI challenger | R9 | Source-derived (reported, not re-verified) | Ch 9 Telangana detail; Ch 10 demand context. | Hyderabad pipeline evidence.
108 | Report 9 · State policies | R9-T03 | Master comparison of state policies | 13 | 8 | Report 9 (full research report) · Part C — Master Comparison Table | R9 | Source-derived (reported, not re-verified) | Ch 9 policy register table, map detail panel and validity chart; simulator incentives. | Incentives and green conditions by state.
109 | Report 9 · State policies | R9-T04 | State attractiveness index | 12 | 10 | Report 9 (full research report) · Part D — Attractiveness Index | R9 | Illustrative / framework / author judgement | Ch 9 attractiveness index (sliders) and map colouring; Ch 10 policy factor. | Weighted state ranking.
110 | Report 10 · Where to build | R10-T01 | Market context: capacity by city, H1 2026 | 7 | 3 | Report 10 (Part 10 research report) · Key Findings | R10 | Source-derived (reported, not re-verified) | Ch 10 context; Ch 1/9 city capacity. | Market size and pipeline by city.
111 | Report 10 · Where to build | R10-T02 | Effective tariff by state at 80% load factor | 9 | 3 | Report 10 (Part 10 research report) · Key Findings | R10 | Mixed: sourced figures plus estimates | Ch 10 power score (tariff half); city detail panel. | Tariff score = 10 × (8.70 − x) ÷ (8.70 − 5.96).
112 | Report 10 · Where to build | R10-T03 | Factor weights by use case | 9 | 5 | Report 10 (Part 10 research report) · Method | R10 | Illustrative / framework / author judgement | Ch 10 weight presets (balanced, AI, interconnection, sustainability). | Use-case rankings.
113 | Report 10 · Where to build | R10-T04 | Inter-hub distances and latency | 6 | 3 | Report 10 (Part 10 research report) · Method | R10 | Calculated (model output) | Ch 10 latency formula drawer. | RTT = 0.014 × km.
114 | Report 10 · Where to build | R10-T05 | Latency table: great-circle km to four hubs and mean RTT | 37 | 7 | Report 10 (Part 10 research report) · Latency table (great-circle km to Mumbai / Delhi / Chennai / Bengaluru → mean RTT) | R10 | Calculated (model output) | Ch 10 latency factor (recomputed in the atlas with haversine). | Latency score per city.
115 | Report 10 · Where to build | R10-T06 | State shortlist: Maharashtra | 4 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › Maharashtra | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
116 | Report 10 · Where to build | R10-T07 | State shortlist: Tamil Nadu | 4 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › Tamil Nadu | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
117 | Report 10 · Where to build | R10-T08 | State shortlist: Karnataka | 4 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › Karnataka | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
118 | Report 10 · Where to build | R10-T09 | State shortlist: Telangana | 3 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › Telangana | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
119 | Report 10 · Where to build | R10-T10 | State shortlist: Andhra Pradesh | 4 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › Andhra Pradesh | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
120 | Report 10 · Where to build | R10-T11 | State shortlist: Uttar Pradesh | 5 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › Uttar Pradesh | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
121 | Report 10 · Where to build | R10-T12 | State shortlist: Haryana | 2 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › Haryana | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
122 | Report 10 · Where to build | R10-T13 | State shortlist: Delhi | 1 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › Delhi | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
123 | Report 10 · Where to build | R10-T14 | State shortlist: Gujarat | 4 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › Gujarat | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
124 | Report 10 · Where to build | R10-T15 | State shortlist: West Bengal | 3 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › West Bengal | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
125 | Report 10 · Where to build | R10-T16 | State shortlist: Kerala | 2 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › Kerala | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
126 | Report 10 · Where to build | R10-T17 | State shortlist: Odisha | 2 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › Odisha | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
127 | Report 10 · Where to build | R10-T18 | State shortlist: Rajasthan | 2 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › Rajasthan | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
128 | Report 10 · Where to build | R10-T19 | State shortlist: Madhya Pradesh | 2 | 10 | Report 10 (Part 10 research report) · State-by-state shortlists › Madhya Pradesh | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
129 | Report 10 · Where to build | R10-T20 | Secondary states shortlist | 8 | 6 | Report 10 (Part 10 research report) · State-by-state shortlists › Secondary states | R10 | Mixed: sourced figures plus estimates | Ch 10 map dots, detail panel and ranking table (site attributes and scores). | Filter pass/fail, factor scores and tier for each city in the state.
130 | Report 10 · Where to build | R10-T21 | National master table (default weights) | 50 | 10 | Report 10 (Part 10 research report) · National master table (default weights) | R10 | Calculated (model output) | Ch 10 ranking table; worked-example workbook. | National rank and tier.
131 | Report 10 · Where to build | R10-T22 | Alternate weightings and rank stability | 23 | 6 | Report 10 (Part 10 research report) · Alternate weightings and rank stability | R10 | Calculated (model output) | Ch 10 "Top picks by use case"; Monte Carlo context. | Rank stability across weightings.
132 | Report 11 · Forecast to 2035 | R11-T01 | Historical capacity series | 10 | 4 | Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.1 Historical series | R11 | Mixed: sourced figures plus estimates | Ch 11 history points on the capacity chart. | Fitted CAGR (27.9%) and logistic rate.
133 | Report 11 · Forecast to 2035 | R11-T02 | CAGR model: forward scenarios from 1,611 MW | 3 | 6 | Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.2 Model (a): CAGR, C(t) = C₀(1+g)^t | R11 | Calculated (model output) | Ch 11 CAGR model option. | Capacity path under constant growth.
134 | Report 11 · Forecast to 2035 | R11-T03 | Logistic model parameters | 3 | 4 | Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.3 Model (b): logistic S-curve, C(t) = K / (1 + e^(−r(t − t₀))) | R11 | Proxy / estimate | Ch 11 S-curve sliders (K, r). | Logistic midpoint t₀.
135 | Report 11 · Forecast to 2035 | R11-T04 | Logistic model output (MW) | 10 | 4 | Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.3 Model (b): logistic S-curve, C(t) = K / (1 + e^(−r(t − t₀))) | R11 | Calculated (model output) | Ch 11 S-curve model option. | Capacity path to 2035.
136 | Report 11 · Forecast to 2035 | R11-T05 | Forecast conversion evidence (backtest) | 6 | 5 | Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.4 Model (c): pipeline conversion, C(t+1) = C(t) + Σ P_stage(t − L) × c_stage | R11 | Mixed: sourced figures plus estimates | Ch 11 haircut KPI (0.58–0.87×). | Delivery haircut on forecasts.
137 | Report 11 · Forecast to 2035 | R11-T06 | Pipeline conversion parameters | 3 | 3 | Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.4 Model (c): pipeline conversion, C(t+1) = C(t) + Σ P_stage(t − L) × c_stage | R11 | Proxy / estimate | Ch 11 pipeline-conversion sliders. | Expected delivered MW from pipeline.
138 | Report 11 · Forecast to 2035 | R11-T07 | Pipeline-conversion path to 2030 (MW) | 3 | 6 | Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.4 Model (c): pipeline conversion, C(t+1) = C(t) + Σ P_stage(t − L) × c_stage | R11 | Calculated (model output) | Ch 11 pipeline model option. | Capacity to 2030.
139 | Report 11 · Forecast to 2035 | R11-T08 | Integrated capacity path 2026–2035 (MW IT) | 3 | 11 | Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.5 Integrated capacity path | R11 | Calculated (model output) | Ch 11 integrated base case (default chart). | Base / low / high capacity path.
140 | Report 11 · Forecast to 2035 | R11-T09 | Published forecasts compared | 14 | 6 | Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.6 Published forecasts compared | R11 | Source-derived (reported, not re-verified) | Ch 11 "Published forecasts compared" chart. | Our base vs consultant median.
141 | Report 11 · Forecast to 2035 | R11-T10 | Electricity, base case: MW, utilisation, PUE, TWh and share | 10 | 8 | Report 11 (Part 11 research report) · 2. Electricity (TWh) and share of the grid | R11 | Calculated (model output) | Ch 11 electricity and share outputs. | TWh and % of national demand.
142 | Report 11 · Forecast to 2035 | R11-T11 | Electricity scenarios | 3 | 6 | Report 11 (Part 11 research report) · 2. Electricity (TWh) and share of the grid | R11 | Calculated (model output) | Ch 11 scenario comparison. | Low/base/high electricity.
143 | Report 11 · Forecast to 2035 | R11-T12 | State-level electricity shares, base case | 6 | 7 | Report 11 (Part 11 research report) · 2. Electricity (TWh) and share of the grid | R11 | Proxy / estimate | Ch 11 state share outputs (denominators are estimates). | Grid stress by state.
144 | Report 11 · Forecast to 2035 | R11-T13 | Grid emission factor history (CEA) | 5 | 2 | Report 11 (Part 11 research report) · 3. Carbon trajectory | R11 | Source-derived (reported, not re-verified) | Ch 11 carbon inputs; all calculators (0.710). | Grid carbon trend.
145 | Report 11 · Forecast to 2035 | R11-T14 | Emission-factor paths | 3 | 4 | Report 11 (Part 11 research report) · 3. Carbon trajectory | R11 | Proxy / estimate | Ch 11 EF slider paths. | Future grid carbon.
146 | Report 11 · Forecast to 2035 | R11-T15 | Emissions, base case | 10 | 6 | Report 11 (Part 11 research report) · 3. Carbon trajectory | R11 | Calculated (model output) | Ch 11 carbon outputs. | Net and location-based CO₂.
147 | Report 11 · Forecast to 2035 | R11-T16 | Build-cost data points | 8 | 4 | Report 11 (Part 11 research report) · 4. Costs: build cost per MW and GPU-hour prices › 4.1 Build cost | R11 | Source-derived (reported, not re-verified) | Ch 11 cost inputs. | Base cost and learning test.
148 | Report 11 · Forecast to 2035 | R11-T17 | Build-cost path (₹ crore/MW) | 3 | 8 | Report 11 (Part 11 research report) · 4. Costs: build cost per MW and GPU-hour prices › 4.1 Build cost | R11 | Calculated (model output) | Ch 11 cost outputs. | ₹ crore per MW path.
149 | Report 11 · Forecast to 2035 | R11-T18 | Cumulative facility capex, base case | 10 | 5 | Report 11 (Part 11 research report) · 4. Costs: build cost per MW and GPU-hour prices › 4.1 Build cost | R11 | Calculated (model output) | Ch 11 capex outputs. | Cumulative investment.
150 | Report 11 · Forecast to 2035 | R11-T19 | India H100 commercial rates | 4 | 2 | Report 11 (Part 11 research report) · 4. Costs: build cost per MW and GPU-hour prices › 4.2 GPU-hour prices | R11 | Source-derived (reported, not re-verified) | Ch 7 market prices; Ch 11 GPU path start. | GPU price base.
151 | Report 11 · Forecast to 2035 | R11-T20 | GPU-hour price path (₹) | 4 | 6 | Report 11 (Part 11 research report) · 4. Costs: build cost per MW and GPU-hour prices › 4.2 GPU-hour prices | R11 | Calculated (model output) | Ch 11 GPU price outputs. | GPU-hour price path.
152 | Report 11 · Forecast to 2035 | R11-T21 | Dry/liquid share, WUE mix and national water | 10 | 4 | Report 11 (Part 11 research report) · 5. Water demand by city (MLD) | R11 | Calculated (model output) | Ch 11 water outputs (Bass diffusion). | National on-site MLD.
153 | Report 11 · Forecast to 2035 | R11-T22 | City water demand and supply | 8 | 8 | Report 11 (Part 11 research report) · 5. Water demand by city (MLD) | R11 | Mixed: sourced figures plus estimates | Ch 11 city water outputs. | DC share of city water supply.
154 | Report 11 · Forecast to 2035 | R11-T23 | Pipeline shares by city | 7 | 3 | Report 11 (Part 11 research report) · 6. Where new capacity goes, city by city | R11 | Source-derived (reported, not re-verified) | Ch 11 city allocation (2026–30). | Where new MW go.
155 | Report 11 · Forecast to 2035 | R11-T24 | Illustrative city scores for allocation | 8 | 2 | Report 11 (Part 11 research report) · 6. Where new capacity goes, city by city | R11 | Illustrative / framework / author judgement | Ch 11 city allocation (illustrative scores). | Softmax share of growth.
156 | Report 11 · Forecast to 2035 | R11-T25 | City capacity forecast | 10 | 6 | Report 11 (Part 11 research report) · 6. Where new capacity goes, city by city | R11 | Calculated (model output) | Ch 11 city capacity outputs. | City MW 2030 and 2035.
157 | Report 11 · Forecast to 2035 | R11-T26 | Driver-based 2030 forecasts | 4 | 2 | Report 11 (Part 11 research report) · 7. Demand drivers (regression) | R11 | Calculated (model output) | Ch 11 driver cross-check (text). | Demand-side view of 2030.
158 | Report 11 · Forecast to 2035 | R11-T27 | Integrated base-case table 2026–2035 | 10 | 11 | Report 11 (Part 11 research report) · 8. Integrated base-case table (2026–2035) [M] | R11 | Calculated (model output) | Ch 11 integrated table and KPIs. | Year-by-year base case.
159 | Report 11 · Forecast to 2035 | R11-T28 | Calculator parameters and Monte Carlo distributions | 30 | 7 | Report 11 (Part 11 research report) · 9. Parameter table for the calculator, with Monte Carlo distributions | R11 | Proxy / estimate | Ch 11 slider ranges and Monte Carlo band. | Uncertainty range.
160 | Report 12 · Water and energy | R12-T01 | Water definitions and metrics | 9 | 4 | Report 12 (Part 12 research report) · 1. Direct (on-site) water › 1.1 Definitions and metrics | R12 | Source-derived, verified | Ch 12 definitions; Data register. | Report withdrawal and consumption separately.
161 | Report 12 · Water and energy | R12-T02 | Cooling-tower water components and physics | 15 | 7 | Report 12 (Part 12 research report) · 1. Direct (on-site) water › 1.2 Components and physics | R12 | Proxy / estimate | Ch 12 "Inside a cooling tower" calculator. | Tower WUE vs cycles of concentration.
162 | Report 12 · Water and energy | R12-T03 | Published WUE and water values | 20 | 4 | Report 12 (Part 12 research report) · 1. Direct (on-site) water › 1.3 Published WUE and water values | R12 | Source-derived, verified | Ch 12 power-vs-water chart (fleet dots); Data register verified figures. | Benchmark WUE/PUE.
163 | Report 12 · Water and energy | R12-T04 | Water per AI query | 5 | 5 | Report 12 (Part 12 research report) · 1. Direct (on-site) water › 1.4 Water per AI query | R12 | Mixed: sourced figures plus estimates | Ch 12 "Water behind one AI prompt" chart. | Per-prompt water with grid water.
164 | Report 12 · Water and energy | R12-T05 | Water intensity of electricity generation | 13 | 4 | Report 12 (Part 12 research report) · 2. Indirect (off-site) water › 2.1 Water intensity of generation | R12 | Mixed: sourced figures plus estimates | Ch 12 "Where grid water comes from" chart. | Water intensity by generation source.
165 | Report 12 · Water and energy | R12-T06 | Indian grid-average water intensity, FY25 | 7 | 4 | Report 12 (Part 12 research report) · 2. Indirect (off-site) water › 2.2 Indian grid-average water intensity | R12 | Calculated (model output) | Ch 12 grid-water chart and calculator default (3.0 L/kWh). | Indian grid water intensity.
166 | Report 12 · Water and energy | R12-T07 | State grid water proxies | 6 | 4 | Report 12 (Part 12 research report) · 2. Indirect (off-site) water › 2.2 Indian grid-average water intensity | R12 | Proxy / estimate | Ch 12 state ranges chart and calculator grid options. | State grid water.
167 | Report 12 · Water and energy | R12-T08 | Source WUE by case | 4 | 5 | Report 12 (Part 12 research report) · 2. Indirect (off-site) water › 2.3 Source WUE formula | R12 | Calculated (model output) | Ch 12 source WUE in power-vs-water view. | Total water per kWh of IT.
168 | Report 12 · Water and energy | R12-T09 | Embedded water (scope 3) | 4 | 3 | Report 12 (Part 12 research report) · 2. Indirect (off-site) water › 2.4 Embedded water (scope 3), order of magnitude | R12 | Mixed: sourced figures plus estimates | Reference only (scope 3 water). | Embedded water share.
169 | Report 12 · Water and energy | R12-T10 | Water and energy by cooling technology (India) | 14 | 7 | Report 12 (Part 12 research report) · 3. Water by cooling technology | R12 | Proxy / estimate | Ch 12 power-vs-water boxes; calculator design defaults. | PUE and WUE ranges per technology.
170 | Report 12 · Water and energy | R12-T11 | Wet-mode hours and design wet-bulb by city | 8 | 4 | Report 12 (Part 12 research report) · 3. Water by cooling technology | R12 | Proxy / estimate | Ch 12 wet-hours chart; checked by the 8,760-hour model. | Adiabatic water by city.
171 | Report 12 · Water and energy | R12-T12 | Peak water factors | 4 | 6 | Report 12 (Part 12 research report) · 4. Peak water demand › 4.1 Peak factors (calculator inputs) | R12 | Calculated (model output) | Ch 12 "Peaks size the pipes" chart; calculator peak factors. | Peak-day and peak-hour water.
172 | Report 12 · Water and energy | R12-T13 | IT load profile archetypes | 5 | 5 | Report 12 (Part 12 research report) · 5. Hourly water and electricity profiles › 5.1 IT load profile archetypes | R12 | Source-derived, verified | Ch 12 utilisation assumptions. | Average IT load by archetype.
173 | Report 12 · Water and energy | R12-T14 | Hot-day hourly profile: 50 MW Hyderabad, adiabatic | 13 | 7 | Report 12 (Part 12 research report) · 5. Hourly water and electricity profiles › 5.3 Hot-day profile: 50 MW hyperscale, Hyderabad, adiabatic (Example B), May design day | R12 | Calculated (model output) | Ch 12 "One hot day, hour by hour" chart. | Hourly water, power and price; dry-at-noon saving.
174 | Report 12 · Water and energy | R12-T15 | Tariff time-of-day structures | 3 | 3 | Report 12 (Part 12 research report) · 5. Hourly water and electricity profiles › 5.4 Tariff time structures | R12 | Source-derived, verified | Ch 12 hourly context; Ch 5 load shift. | ToD saving potential.
175 | Report 12 · Water and energy | R12-T16 | DISCOM HT/EHT tariffs, FY2025-26 | 7 | 6 | Report 12 (Part 12 research report) · 6. Grid electricity options in India › 6.1 DISCOM HT/EHT tariffs (FY2025-26 unless noted) | R12 | Mixed: sourced figures plus estimates | Ch 12 cost-vs-water chart (landed ₹/kWh). | Landed power cost by state and category.
176 | Report 12 · Water and energy | R12-T17 | Open access and procurement options | 15 | 6 | Report 12 (Part 12 research report) · 6. Grid electricity options in India › 6.2 Open access and procurement options | R12 | Mixed: sourced figures plus estimates | Ch 12 cost-vs-water chart (procurement options). | Landed cost of each procurement route.
177 | Report 12 · Water and energy | R12-T18 | Supply voltage by facility size | 5 | 3 | Report 12 (Part 12 research report) · 6. Grid electricity options in India › 6.3 Reliability and connection | R12 | Proxy / estimate | Ch 12 calculator contract demand note. | Supply voltage per project size.
178 | Report 12 · Water and energy | R12-T19 | Typical energy parameter values | 14 | 5 | Report 12 (Part 12 research report) · 7. Energy calculations › 7.2 Typical parameter values | R12 | Mixed: sourced figures plus estimates | Ch 12 calculator parameters. | Energy, MVA, DG and UPS sizing.
179 | Report 12 · Water and energy | R12-T20 | Scale snapshot by archetype | 4 | 8 | Report 12 (Part 12 research report) · 7. Energy calculations › 7.3 Scale snapshot | R12 | Calculated (model output) | Reference for Ch 12 calculator. | Energy and connection per archetype.
180 | Report 12 · Water and energy | R12-T21 | Example A: 20 MW Mumbai colo, step by step | 13 | 4 | Report 12 (Part 12 research report) · 8. Worked examples › Example A: 20 MW IT colocation, Mumbai (Navi Mumbai), water-cooled chillers + open cooling towers | R12 | Calculated (model output) | Ch 12 "Where the water goes" and cost-vs-water charts (Example A). | Water and cost for a Mumbai colo.
181 | Report 12 · Water and energy | R12-T22 | Example A: landed electricity cost by option | 5 | 5 | Report 12 (Part 12 research report) · 8. Worked examples › Example A: 20 MW IT colocation, Mumbai (Navi Mumbai), water-cooled chillers + open cooling towers | R12 | Calculated (model output) | Ch 12 cost-vs-water chart (Example A dots). | Cheapest procurement route.
182 | Report 12 · Water and energy | R12-T23 | Example B: 50 MW Hyderabad hyperscale, step by step | 13 | 4 | Report 12 (Part 12 research report) · 8. Worked examples › Example B: 50 MW IT hyperscale, Hyderabad, air-side economiser / adiabatic-assisted cooling | R12 | Calculated (model output) | Ch 12 charts (Example B) and hourly profile. | Water and cost for a Hyderabad hyperscale site.
183 | Report 12 · Water and energy | R12-T24 | Example B: landed electricity cost by option | 5 | 4 | Report 12 (Part 12 research report) · 8. Worked examples › Example B: 50 MW IT hyperscale, Hyderabad, air-side economiser / adiabatic-assisted cooling | R12 | Calculated (model output) | Ch 12 cost-vs-water chart (Example B dots). | Cheapest procurement route.
184 | Report 12 · Water and energy | R12-T25 | Example C: 100 MW Bengaluru AI campus, step by step | 15 | 4 | Report 12 (Part 12 research report) · 8. Worked examples › Example C: 100 MW IT AI campus, Bengaluru (alt.: Visakhapatnam), direct-to-chip liquid cooling + dry coolers | R12 | Calculated (model output) | Ch 12 charts (Example C). | Water and cost for a Bengaluru AI campus.
185 | Report 12 · Water and energy | R12-T26 | Example C: landed electricity cost by option | 3 | 4 | Report 12 (Part 12 research report) · 8. Worked examples › Example C: 100 MW IT AI campus, Bengaluru (alt.: Visakhapatnam), direct-to-chip liquid cooling + dry coolers | R12 | Calculated (model output) | Ch 12 cost-vs-water chart (Example C dots). | Cheapest procurement route.
186 | Report 12 · Water and energy | R12-T27 | Bottom line across the three examples | 5 | 4 | Report 12 (Part 12 research report) · 8. Worked examples › Example C: 100 MW IT AI campus, Bengaluru (alt.: Visakhapatnam), direct-to-chip liquid cooling + dry coolers | R12 | Calculated (model output) | Ch 12 "Where the water goes" chart. | Direct vs indirect water across examples.
187 | Report 12 · Water and energy | R12-T28 | Data gaps and how to close them | 9 | 3 | Report 12 (Part 12 research report) · Data gaps and how to close them | R12 | Illustrative / framework / author judgement | Data register "Data gaps" tab. | Next data to collect.
188 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T01 | Report 1: Five ways to classify a data centre | 5 | 3 | Atlas Ch 1 (from Report 1) | Atlas R1-R9 | Illustrative / framework / author judgement | Shown in atlas Ch 1 Types (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
189 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T02 | Report 1: Six data-centre business models | 6 | 8 | Atlas Ch 1 (from Report 1); industry sources | Atlas R1-R9 | Mixed: sourced figures plus estimates | Shown in atlas Ch 1 Types (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
190 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T03 | Report 1: Uptime Tier levels | 4 | 5 | Atlas Ch 1 (from Report 1); Uptime Institute Tier Standard | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 1 Types (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
191 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T04 | Report 1: Share of global data-centre capacity by owner type (%) | 4 | 4 | Synergy Research Group (Apr 2026); 2031 is a projection | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 1 Types (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
192 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T05 | Report 1: India capacity by city, H1 2026 (MW IT) | 8 | 3 | Cushman & Wakefield India Data Centre H1 2026 Update | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 1 Types (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
193 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T06 | Report 2: Global data-centre electricity (TWh) | 3 | 2 | IEA, Energy and AI (Apr 2025), base case; 2035 extrapolated | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
194 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T07 | Report 2: Share of facility electricity by use and facility class (%) | 4 | 5 | Series synthesis from PUE ranges and IEA component shares (estimate) | Atlas R1-R9 | Proxy / estimate | Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
195 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T08 | Report 2: Rack power density by design (kW per rack) | 6 | 2 | Nvidia specifications and GTC roadmap; industry estimates (Rubin) | Atlas R1-R9 | Proxy / estimate | Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
196 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T09 | Report 2: Power-chain losses, grid to chip | 4 | 2 | Atlas Ch 2 (Report 2); typical industry ranges | Atlas R1-R9 | Proxy / estimate | Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
197 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T10 | Report 2: Energy per workload | 7 | 3 | Atlas Ch 2 (from Report 2) | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
198 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T11 | Report 2: Conventional vs AI data centre | 9 | 3 | Atlas Ch 2 (from Report 2) | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
199 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T12 | Report 2: Training vs inference sites | 5 | 3 | Atlas Ch 2 (from Report 2) | Atlas R1-R9 | Illustrative / framework / author judgement | Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
200 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T13 | Report 3: Heat a cubic metre of fluid carries per degree (kJ/m³·K) | 5 | 2 | Standard physical properties | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
201 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T14 | Report 3: Heat-rejection options: water, energy and fit for India | 6 | 4 | Atlas Ch 3 (from Report 3) | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
202 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T15 | Report 3: Liquid cooling technologies compared | 5 | 5 | Atlas Ch 3 (from Report 3); vendor-reported PUE | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
203 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T16 | Report 3: Liquid-cooling manufacturer revenue (US$ bn) | 3 | 2 | Dell'Oro Group (Jan 2026); 2029 projection | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
204 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T17 | Report 3: Cooling-sector acquisitions 2024–26 | 5 | 2 | Company announcements | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
205 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T18 | Report 3: India HFC phase-down schedule (Kigali Amendment) | 6 | 2 | Kigali Amendment to the Montreal Protocol (India, Group 2) | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
206 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T19 | Report 3: City design temperatures used in the cooling chapter | 7 | 3 | Atlas Ch 3 (from Report 3); indicative 0.4% summer conditions (estimate) | Atlas R1-R9 | Proxy / estimate | Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
207 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T20 | Report 3: What to use where in India | 5 | 4 | Atlas Ch 3 (from Report 3) | Atlas R1-R9 | Illustrative / framework / author judgement | Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
208 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T21 | Report 3: Practical rack-density ceiling by cooling method (kW) | 5 | 2 | Atlas Ch 3 cooling selector (estimate) | Atlas R1-R9 | Proxy / estimate | Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
209 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T22 | Report 4: Bengaluru's water sources | 4 | 2 | Atlas Ch 4 (from Report 4); BWSSB, Karnataka groundwater assessment | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
210 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T23 | Report 4: Grid connection by contract demand (Karnataka) | 4 | 3 | KERC conditions of supply (as reported) | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
211 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T24 | Report 4: Water use compared with other users (MLD) | 10 | 2 | Atlas Ch 4 (from Report 4) | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
212 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T25 | Report 4: Bengaluru data centres' water use today: estimates (MLD) | 5 | 2 | Down To Earth; Karnataka IT dept; series model; WELL Labs | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
213 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T26 | Report 4: Scaling to Karnataka's 1 GW target: on-site water by cooling choice (MLD) | 3 | 5 | Report 4 model, 75% utilisation | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
214 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T27 | Report 4: Bengaluru campus central cases | 3 | 8 | Report 4 model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
215 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T28 | Report 4: Recommended Karnataka roadmap | 3 | 3 | Atlas Ch 4 (from Report 4) | Atlas R1-R9 | Illustrative / framework / author judgement | Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
216 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T29 | Report 5: Carbon of 1 TWh of data-centre load, by supply (Mt CO₂) | 8 | 2 | Report 5 comparison (CEA, Ember, IPCC) | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
217 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T30 | Report 5: Karnataka illustrative hourly grid intensity, dry season (gCO₂/kWh) | 24 | 3 | Modelled from a third-party dashboard; no official hourly factor exists | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
218 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T31 | Report 5: Lifecycle carbon by source (gCO₂e/kWh) | 6 | 2 | IPCC AR5 Annex III medians | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
219 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T32 | Report 5: Water consumed by generation source (L/MWh) | 6 | 2 | CSE, NREL, CEA research | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
220 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T33 | Report 5: Microsoft Scope 2 emissions (Mt CO₂e) | 2 | 3 | Microsoft sustainability reports | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
221 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T34 | Report 5: Carbon per IT-kWh, worked (CUE = PUE × grid factor) | 4 | 2 | Atlas Ch 5 (from Report 5) | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
222 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T35 | Report 5: Five-factor scorecard weights | 5 | 2 | Report 5 framework | Atlas R1-R9 | Illustrative / framework / author judgement | Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
223 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T36 | Report 6: Monthly withdrawal, 50 MW evaporative site (MLD) | 12 | 2 | Report 6 model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
224 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T37 | Report 6: Scarcity-weighted water footprint, 50 MW (Mm³-eq/yr) | 5 | 3 | Report 6 model; illustrative AWARE-style weights | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
225 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T38 | Report 6: Water per AI prompt, by boundary (mL) | 6 | 2 | Google; Li et al.; Mistral LCA; Report 6 model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
226 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T39 | Report 6: Impact scorecard | 6 | 3 | Atlas Ch 6 (from Report 6) | Atlas R1-R9 | Illustrative / framework / author judgement | Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
227 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T40 | Report 6: Bengaluru scenarios: site and source water | 4 | 5 | Atlas Ch 6 (from Report 6) model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
228 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T41 | Report 6: Suggested water thresholds | 5 | 4 | Atlas Ch 6 (from Report 6) (proposal) | Atlas R1-R9 | Illustrative / framework / author judgement | Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
229 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T42 | Report 6: Cooling-tower water balance, 50 MW (default CoC 5) | 9 | 2 | Report 6 model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
230 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T43 | Report 7: Data-centre construction cost by market (US$/W) | 12 | 2 | Turner & Townsend Data Centre Cost Index 2025 | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
231 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T44 | Report 7: Capex per MW by category, three cases (₹ crore/MW) | 3 | 8 | Report 7 model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
232 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T45 | Report 7: Capex line by line: A · 20 MW Tier III colo | 12 | 4 | Report 7 model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
233 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T46 | Report 7: Capex line by line: B · 50 MW hyperscale BTS | 12 | 4 | Report 7 model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
234 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T47 | Report 7: Capex line by line: C · 100 MW AI campus | 13 | 4 | Report 7 model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
235 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T48 | Report 7: Colocation opex, Case A (₹ crore a year) | 9 | 2 | Report 7 model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
236 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T49 | Report 7: What moves the colo LCOD (₹ per IT-kWh; base 29.7) | 5 | 3 | Report 7 model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
237 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T50 | Report 7: GPU-hour market prices, H100-class (Oct 2026) | 6 | 2 | IndiaAI; provider price pages; OCPI index | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
238 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T51 | Report 7: Returns by business model | 5 | 4 | Report 7 model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
239 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T52 | Report 7: India vs US vs Singapore | 4 | 4 | C&W, CBRE, JLL, Turner & Townsend | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
240 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T53 | Report 7: Land and power by hub | 5 | 3 | Market reports; state tariff orders | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
241 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T54 | Report 7: GPU cost model inputs | 10 | 2 | Report 7 assumptions | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
242 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T55 | Report 8: Abatement cost by measure, 20 MW Bengaluru colo (₹/tCO₂) | 4 | 2 | Report 8 model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 8 Green (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
243 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T56 | Report 8: PUE thresholds around the world | 10 | 2 | EU, Germany EnEfG, Karnataka, China, Singapore IMDA, MeitY, Uptime | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 8 Green (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
244 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T57 | Report 8: Green upgrade case, 20 MW Bengaluru colo | 10 | 2 | Report 8 model | Atlas R1-R9 | Calculated (model output) | Shown in atlas Ch 8 Green (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
245 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T58 | Report 8: Twelve dimensions of a green data centre | 12 | 4 | Report 8 framework | Atlas R1-R9 | Illustrative / framework / author judgement | Shown in atlas Ch 8 Green (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
246 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T59 | Report 8: Spotting greenwashing | 5 | 3 | Atlas Ch 8 (from Report 8) | Atlas R1-R9 | Illustrative / framework / author judgement | Shown in atlas Ch 8 Green (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
247 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T60 | Report 8: Buying clean power in India | 6 | 3 | Atlas Ch 8 (from Report 8); SECI; KERC | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 8 Green (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
248 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T61 | Report 8: Green rules elsewhere | 5 | 2 | EU, Germany, Singapore, China, India | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 8 Green (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
249 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T62 | Report 8: Indian operators' green disclosures | 5 | 2 | Company reports | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 8 Green (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
250 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T63 | Report 9: State data-centre policy register | 15 | 9 | State policy documents and GRs (Report 9) | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 9 State policies (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
251 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T64 | Report 9: State attractiveness factor scores (0–10) and index | 12 | 10 | Report 9 judgement; index uses report weights 25/15/15/15/10/10/10 | Atlas R1-R9 | Illustrative / framework / author judgement | Shown in atlas Ch 9 State policies (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
252 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T65 | Report 9: Policy validity periods | 13 | 4 | State policies (Report 9) | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 9 State policies (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
253 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T66 | Report 9: Electricity-duty holiday by state (years) | 8 | 2 | State policies | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 9 State policies (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
254 | Atlas-derived tables for Reports 1–9 (charts and calculators) | ATL-T67 | Report 9: The central framework | 6 | 2 | Atlas Ch 9 (from Report 9) | Atlas R1-R9 | Source-derived (reported, not re-verified) | Shown in atlas Ch 9 State policies (chart, table or calculator data built from the report). | Same purpose as the matching report table; restated in the form the atlas displays.
255 | Simulator inputs (Reports 3–9) | SIM-T01 | Simulator assumptions and evidence | 13 | 4 | Atlas simulator (Reports 3–7) | Simulator | Mixed: sourced figures plus estimates | Simulator "Assumptions behind the simulator" table; feeds every simulator output. | Capex, cost per IT-kWh, energy, water, CO₂, MVA and incentives for any design.
256 | Simulator inputs (Reports 3–9) | SIM-T02 | Simulator city parameters | 6 | 12 | Atlas simulator (Reports 3–7) | Simulator | Mixed: sourced figures plus estimates | Simulator model inputs. | Capex, PUE, WUE and costs for each city and workload in the simulator.
257 | Simulator inputs (Reports 3–9) | SIM-T03 | Simulator workload parameters | 3 | 9 | Atlas simulator (Report 7) | Simulator | Mixed: sourced figures plus estimates | Simulator model inputs. | Capex, PUE, WUE and costs for each city and workload in the simulator.
258 | Simulator inputs (Reports 3–9) | SIM-T04 | State incentives modelled in the simulator | 6 | 5 | State policies (Report 9) | Simulator | Source-derived (reported, not re-verified) | Simulator incentive line and policy panel. | Incentive value per year and per IT-kWh.
259 | Key numbers (all reports) | KEY-T01 | Key numbers cheat sheet | 42 | 3 | Atlas Key numbers (all reports) | Key numbers | Mixed: sourced figures plus estimates | Key numbers cheat sheet (searchable list) at the end of the atlas. | Quick reference for the most-used figures; each row names its source.
Tables per report
| Report 1 · Types of data centre | 7
| Report 2 · AI vs conventional | 9
| Report 3 · Cooling | 15
| Report 4 · Bengaluru water and power | 8
| Report 5 · Carbon | 8
| Report 6 · Water impact | 22
| Report 7 · Unit economics | 24
| Report 8 · Green data centres | 12
| Report 9 · State policies | 4
| Report 10 · Where to build | 22
| Report 11 · Forecast to 2035 | 28
| Report 12 · Water and energy | 28
| Atlas-derived tables for Reports 1–9 (charts and calculators) | 67
| Simulator inputs (Reports 3–9) | 4
| Key numbers (all reports) | 1
| Total | 259

## How to read
How these tables feed the atlas
Every table carries three lines under its title: data basis, how it is used in the atlas, and what it is used to derive. The Index repeats them as filterable columns.
Data basis
Category | Meaning | How to treat it
Source-derived, verified | Figures checked against the primary document during the research (Report 12 labelled these one by one). | Safe to cite; still note the date.
Source-derived (reported, not re-verified) | Figures taken from a named source (consultancy, regulator, company, IEA, etc.) as cited in the report, without a check against the original. | Cite with the source; confirm against the original before decisions.
Mixed: sourced figures plus estimates | A table combining reported numbers with analyst estimates or ranges (for example EHV distances or design temperatures alongside tariffs). | Use the sourced columns as data and the estimated ones as placeholders.
Proxy / estimate | Engineering ranges, analogues, typical values or assumptions standing in for missing Indian data. | Indicative only; replace with measured or official data when available.
Illustrative / framework / author judgement | Scorecards, indices, weights, maturity levels, thresholds and recommendations created by the research series. | A method, not data; change the weights or scores to suit your view.
Calculated (model output) | Results of the series' formulas (worked examples, capex stacks, LCOD, forecasts, rankings, water balances). | Only as good as the inputs; rerun when inputs change.
Count of tables by report and basis (live)
Report | Source-derived, verified | Source-derived (reported, not re-verified) | Mixed: sourced figures plus estimates | Proxy / estimate | Illustrative / framework / author judgement | Calculated (model output) | Total
Report 1 · Types of data centre | 0 | 5 | 2 | 0 | 0 | 0 | 7
Report 2 · AI vs conventional | 0 | 4 | 2 | 0 | 3 | 0 | 9
Report 3 · Cooling | 0 | 6 | 6 | 2 | 1 | 0 | 15
Report 4 · Bengaluru water and power | 0 | 1 | 1 | 1 | 1 | 4 | 8
Report 5 · Carbon | 0 | 2 | 4 | 0 | 1 | 1 | 8
Report 6 · Water impact | 0 | 5 | 3 | 1 | 5 | 8 | 22
Report 7 · Unit economics | 0 | 6 | 3 | 1 | 0 | 14 | 24
Report 8 · Green data centres | 0 | 5 | 1 | 2 | 3 | 1 | 12
Report 9 · State policies | 0 | 3 | 0 | 0 | 1 | 0 | 4
Report 10 · Where to build | 0 | 1 | 16 | 0 | 1 | 4 | 22
Report 11 · Forecast to 2035 | 0 | 5 | 3 | 5 | 1 | 14 | 28
Report 12 · Water and energy | 4 | 0 | 6 | 5 | 1 | 12 | 28
Atlas-derived tables for Reports 1–9 (charts and calculators) | 0 | 30 | 1 | 5 | 10 | 21 | 67
Simulator inputs (Reports 3–9) | 0 | 1 | 3 | 0 | 0 | 0 | 4
Key numbers (all reports) | 0 | 0 | 1 | 0 | 0 | 0 | 1
Total | 4 | 74 | 52 | 22 | 28 | 79 | 259
Report → atlas chapter → what the atlas derives
Report | Atlas chapter and tools | Main things the atlas derives from it
Report 1 · Types | Ch 1: type explorer, type finder, Tier clock, capacity-share and India-by-city charts | Which type to build; downtime per Tier; India in global context
Report 2 · AI vs conventional | Ch 2: energy split chart, rack inspector, density chart, workload table, comparison tables | Rack power consequences; AI vs conventional design differences
Report 3 · Cooling | Ch 3: cooling chain, warm-water explorer, cooling selector, heat-rejection and liquid tables; simulator PUE/WUE functions | Cooling design per city and density; PUE and WUE inputs
Report 4 · Bengaluru | Ch 4: campus calculator, water comparisons, 1 GW scaling, 24-hour day | Energy, MVA, water and share of Karnataka resources per campus
Report 5 · Carbon | Ch 5: TWh-seven-ways chart, Karnataka hourly curve, load-shift calculator, five-factor scorecard | Carbon and water per TWh by source, time and place
Report 6 · Water impact | Ch 6: tower water balance, seasonal chart, scarcity footprint, impact scorecard, water you can picture | Withdrawal vs consumption; scarcity-weighted impact; thresholds
Report 7 · Unit economics | Ch 7: build-cost chart, capex stacks, LCOD calculator, tornado, GPU-hour calculator; simulator costs | Capex/MW, LCOD, break-even rent, GPU-hour cost, returns
Report 8 · Green | Ch 8: twelve dimensions, green upgrade calculator, abatement chart, PUE thresholds, maturity radar | Payback and abatement cost of going green
Report 9 · State policies | Ch 9: policy table, India map, attractiveness index, validity and incentive charts; simulator incentives | State ranking and incentive value
Report 10 · Where to build | Ch 10: ranking engine (filters, min–max, weights, Monte Carlo), map and city table; worked-example workbook | City scores, tiers and stability by use case
Report 11 · Forecast | Ch 11: forecast engine (CAGR, S-curve, pipeline), electricity, carbon, cost, GPU, water and city outputs | Capacity and impacts to 2035 with uncertainty band
Report 12 · Water & energy | Ch 12: power-vs-water chart, hourly day, 8,760-hour histogram, grid water, cost-vs-water, peaks, tower and site calculators | Direct vs indirect water, peaks, landed power cost by procurement route

## R1
Report 1 · Types of data centre
7 tables. Source line under each title; "Note" gives the context sentence from the report.
R1-T01 Data-centre types by ownership and business model
Source: Report 1 (full research report) · 1. Types of Data Centre › 1.1 Deep analysis of the types: what exists, what dominates globally, and why
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 1 "Type explorer" cards (how it works, cost, strengths, users) and the Type finder rules.
Used to derive: Which business model fits a project size and workload.
Type | How it works | Typical scale / density | Cost structure | Advantages | Disadvantages | Typical users
Enterprise / on-premises | Organisation owns and runs its own facility (server room up to a corporate campus) | Under 1 MW to about 20 MW; modal rack about 7.5 kW (Uptime 2025) | All capex borne by the owner; opex for power, staff and maintenance; low utilisation is common | Full control, data sovereignty, custom compliance | Poor economies of scale, older and less efficient plant, hard to upgrade for AI density | Banks, government, defence, large manufacturers, hospitals
Retail colocation | Operator leases racks, cages or suites with power, cooling and security; tenant brings servers | Facilities of 5–50 MW; customers take 1 rack to under 1 MW | Tenant pays monthly rent per rack/kW plus interconnection; operator carries building capex | Converts capex to opex, carrier-neutral interconnection, fast deployment | Higher per-kW price, less control, contract lock-in | Enterprises, BFSI, network operators, SaaS firms
Wholesale colocation / build-to-suit | Operator leases whole halls or buildings, often to a single hyperscaler on long leases | 10–100+ MW per building, campuses of hundreds of MW to GW | Operator funds the build (often project-financed against an anchor lease); tenant often pays power at cost plus rent | Speed to market for hyperscalers, bankable long-term cash flows | Concentrated tenant risk, thin margins, power-procurement exposure | AWS, Microsoft, Google, Meta, Oracle, AI labs, neoclouds
Hyperscale (self-built) | Cloud/internet giants design, own and operate their own campuses | Single buildings of 30–100+ MW; campuses of 1 GW+; AI halls at 50–130+ kW/rack | Huge capex funded from balance sheet; lowest unit cost thanks to scale | Lowest cost per MW, custom hardware, best PUE (larger sites average about 1.44, per Uptime 2025) | Very concentrated power and water demand, local opposition, long grid queues | AWS, Microsoft, Google, Meta, Alibaba, Tencent, Oracle
Managed services / cloud | Provider runs the infrastructure and sells compute or storage "as a service" (IaaS/PaaS, managed hosting, GPU-as-a-Service) | Sits on top of hyperscale or colocation capacity | Customer pays per use; provider absorbs capex | Elastic, no hardware ownership, fast access to GPUs | Egress costs, vendor lock-in, data-residency questions | Start-ups, digital natives, enterprises moving to hybrid
Edge / micro | Small facilities close to users or devices (telecom central offices, towers, factory floors, cities) | 50 kW to about 5 MW; micro/containerised units at single-rack scale | Low capex per site but high cost per kW; many sites to manage | Low latency, data reduction, local resilience | Hard to operate at scale, uneven demand, limited GPU density | Telcos (5G/MEC), CDNs/OTT, retail, payments, industrial IoT
R1-T02 Uptime Tiers: redundancy, availability and downtime
Source: Report 1 (full research report) · 1. Types of Data Centre › 1.1 Deep analysis of the types: what exists, what dominates globally, and why
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 1 "What a Tier buys you" downtime clock.
Used to derive: Downtime hours a year = (1 − availability) × 8,760 per Tier.
Uptime Tier | Redundancy | Concurrently maintainable? | Fault tolerant? | Design-intent availability | Approx. annual downtime | Typical use
Tier I – Basic capacity | N, single path | No | No | 99.671% | ~28.8 hours | Small business, dev/test
Tier II – Redundant components | N+1 components, single path | No | No | 99.741% | ~22 hours | Non-critical enterprise
Tier III – Concurrently maintainable | N+1, multiple paths (one active) | Yes | No | 99.982% | ~1.6 hours | Colocation baseline, cloud, BFSI production
Tier IV – Fault tolerant | 2N / 2(N+1), multiple active paths | Yes | Yes | 99.995% | ~26 minutes | Trading, critical health, national systems
R1-T03 Cooling approaches: density, efficiency and water
Source: Report 1 (full research report) · 1. Types of Data Centre › 1.1 Deep analysis of the types: what exists, what dominates globally, and why
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 3 cooling comparison text; density limits used in the Rack inspector bands.
Used to derive: Practical rack-density ceiling per cooling method.
Cooling approach | How it works | Practical rack density | Efficiency | Water use | Status
Air (CRAC/CRAH, hot/cold aisle, economisers) | Chilled or outside air moved through racks | Up to about 15–20 kW/rack (SBI notes air nears its limits beyond about 15 kW) | Fleet average PUE 1.54 (Uptime 2025); new sites about 1.48 | High if evaporative towers are used; low with dry coolers | Still most of the installed base: about 75% use perimeter air (Uptime 2025)
Rear-door heat exchangers / hybrid | Liquid-cooled coil on the rack door removes heat from the exhaust air | About 20–50 kW | Better than room air | Moderate | Most common "first step" into liquid
Direct-to-chip (DLC) | Cold plates on CPUs/GPUs; coolant loop to a CDU; residual air cooling | 30–130+ kW | PUE about 1.1–1.25 achievable | Low with closed loops and dry coolers | Becoming the standard for AI; about 22% of operators used direct liquid cooling in 2025 (Uptime)
Single-phase immersion | Servers submerged in a dielectric fluid | 50–150+ kW | Very low cooling overhead | Very low | Niche; suits edge, crypto and HPC
Two-phase immersion | Fluid boils at the chip and condenses | 100–250+ kW | Lowest overhead | Very low | Early stage; fluid cost and environmental concerns
R1-T04 Global market share and installed capacity by type (2024–2026)
Source: Report 1 (full research report) · 1. Types of Data Centre › 1.1 Deep analysis of the types: what exists, what dominates globally, and why
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 1 headline numbers and "Who owns the world's capacity" chart; Key numbers.
Used to derive: Global growth and hyperscale share trend to set India in context.
Metric | Value | Source and date
Global data centre capacity | ~103 GW (2025) → ~200 GW (2030), 14% CAGR; ~100 GW added 2026–30 | JLL 2026 Global Data Center Outlook (Jan 2026)
Hyperscale share of capacity | 41% (2024) → 44% (Q1 2025) → nearly half, about 48% (early 2026) → 67% projected by 2031 | Synergy Research (2024; Jun 2025; Apr 2026)
Non-hyperscale colocation share | 22% (2024–25) → 20% (2026); absolute capacity still growing | Synergy Research
Enterprise on-premises share | 56% (2018) → 34% (Q1 2025) → 32% (2026) → 19% by 2031; absolute capacity stable and slightly boosted by on-prem GPUs | Synergy Research
Number of hyperscale data centres | 1,189 (Q1 2025); about 800 more in the known pipeline (2026) | Synergy Research
Concentration | 20 metro/state markets hold 60% of hyperscale capacity; Northern Virginia 11%, Beijing 6% | Synergy Research (Aug 2026)
Big three cloud providers' share of hyperscale capacity | 58% | Synergy Research (Q3 2025)
Hyperscale quarterly capex | ~$142 bn in Q3 2025 | Synergy Research via The Register (Dec 2025)
Global occupancy | ~97%; 77% of capacity under construction pre-leased | JLL (Jan 2026)
APAC capacity | 32 GW → 57 GW by 2030; colocation growing ~19% CAGR; on-prem declining 6% | JLL (Jan 2026)
Liquid-cooling adoption | ~22% of operators use direct liquid cooling; ~75% perimeter air | Uptime Institute 2025 survey
R1-T05 India vs global capacity
Source: Report 1 (full research report) · 1. Types of Data Centre › 1.2 Indian perspective: which types to build, why, and how
Note: India vs. global capacity
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 1 and Overview context; Key numbers (India operational capacity, pipeline).
Used to derive: India's share of global capacity; range of Indian capacity estimates.
Metric | India | Global | Source and date
Operational capacity | ~1.5 GW (MeitY/PIB, 2025); 1,123 MW (JLL, H1 2025); ~1.7 GW (CBRE, end-2025); 1,789 MW in top seven markets (C&W, H1 2026) | ~103 GW (2025) | PIB 13 Mar 2026; JLL; CBRE Apr 2026; C&W Sep 2026
Growth | 375 MW (2020) → ~1.5 GW (2025); 440 MW added in 2025; ~500 MW expected in 2026 | 14% CAGR to 2030 | PIB; CBRE
2030 outlook | 3,860 MW pipeline (509 MW under construction, 3,351 MW planned) to 2030 (C&W); total of ~4.5–6.5 GW (CEEW base cases), ~6.5 GW colocation (SBI), up to ~8 GW (Jefferies) | ~200 GW | C&W; CEEW; SBI; JLL
Development capital needed | US$29.9 bn through 2030 | Up to US$3 trn by 2030 | C&W; JLL
Share of national electricity | ~0.5–0.8% (2024) → ~2.6% (2030) | ~1.5% (2024) → under 3% (2030) | CEEW; IEA
Penetration | ~825,333 people per MW of capacity, among the lowest in APAC | n/a | C&W (Sep 2026)
Colocation vacancy | 14.9% (H1 2026) | ~3% (97% occupancy, per JLL) | C&W; JLL
R1-T06 Key Indian hubs (Cushman & Wakefield, H1 2026)
Source: Report 1 (full research report) · 1. Types of Data Centre › 1.2 Indian perspective: which types to build, why, and how
Note: Key hubs (Cushman & Wakefield, H1 2026)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 1 "India by city" chart; Ch 9 map (live and pipeline MW); Ch 10 demand scores; Ch 11 starting point.
Used to derive: City shares, pipeline-to-stock ratios, forecast anchor (1,789 MW).
Hub | Operational (MW) | Share of 3,860 MW pipeline | Why it is there
Mumbai / Navi Mumbai | 890 (about 50%; expected to pass 1 GW by end-2026) | 45% (1,726 MW) | Most subsea cables, BFSI demand, power availability
Chennai | 214 | 9% (368 MW) | Second subsea cable hub; Tamil Nadu policy
Delhi NCR / Noida | 183 | 10% (387 MW) | Northern demand centre, government, UP incentives
Bengaluru | 162 | 3% (100 MW) | IT/SaaS demand; constrained by water and land
Hyderabad | 151 | 18% (710 MW) | Inland, low seismic risk, Telangana power policy, Microsoft/AWS regions
Pune | 133 | 7% (258 MW) | Mumbai overflow, AWS/Microsoft presence
Kolkata | 22 | 2% | Eastern gateway; WB policy promotes edge
Visakhapatnam (emerging) | Small today | Gigawatt-scale campuses announced | New east-coast subsea gateway, Andhra Pradesh incentives
R1-T07 State policies: key terms
Source: Report 1 (full research report) · 1. Types of Data Centre › 1.2 Indian perspective: which types to build, why, and how
Note: State policies (key terms)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Superseded by Report 9 tables; feeds Ch 9 policy register.
Used to derive: Early comparison of state incentives.
State | Policy | Key incentives | Notes
Maharashtra | IT/ITeS Policy 2023 (data centres treated as IT units, with essential-service status) | 100% stamp-duty exemption; electricity-duty exemption (described as permanent in 2023, while a June 2026 notification cites 20 years); ₹1/unit power subsidy for 5 years outside Zone I; renewable open access | Hosts about 50% of capacity; green data centre parks policy reported
Tamil Nadu | Data Centre Policy 2021 | Eligibility above ₹500 crore and at least 30% renewables; 100% electricity-tax subsidy for 5 years; dual grid for 50 MW+; land and stamp-duty concessions | Policy window ended March 2026; no extension notified as of April 2026
Telangana | Data Centres Policy 2016 | Power at cost of generation; dual grid; exemption from power cuts; renewable open access; building-fee and lease-rental rebates | S&P Global rates it India's most attractive data centre policy package
Uttar Pradesh | DC Policy 2021 → new policy approved 6 Jul 2026 | 2021: capital and interest subsidies, 100% stamp duty, 10-year electricity-duty waiver, wheeling/transmission relief (about ₹21,343 crore of projects approved). 2026: targets 2 GW and more than ₹2 trillion, covers edge data centres, AI-compute and green incentives, 50% renewables target by 2030 | Noida is the main northern hub
West Bengal | DC Policy 2021 | 100% stamp duty and registration; 5-year electricity-duty waiver; industrial tariff; dual grid; preferential incentives for edge data centres in IT/industrial parks | 5-year term ran to about September 2026
Andhra Pradesh | DC Policy 4.0 (2024–29) | 100% net SGST reimbursement or 10% capital subsidy; 100% stamp duty; industrial tariff; dual grid via PPP with VGF; custom packages for mega projects over 50 MW | Target given as 200 MW in the G.O. and "up to 1 GW" in the annexure; Vizag is the anchor
Gujarat | IT/ITeS Policy 2022–27 | Capex support of 25% up to ₹150 crore for greenfield Tier III+ data centres; ₹1/unit power subsidy for 5 years; 100% electricity-duty reimbursement for 5 years | Jamnagar mega-campus

## R2
Report 2 · AI vs conventional
9 tables. Source line under each title; "Note" gives the context sentence from the report.
R2-T01 Electricity split by subsystem and facility class
Source: Report 2 (full research report) · Section 1: Anatomy of Data Centre Consumption › 1.1 Electricity breakdown by subsystem
Note: Typical percentage splits by facility class. These are the author's synthesis, derived from PUE ranges and the IEA component shares. They are indicative, not measured.
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 2 "Where the power goes, by facility class" chart.
Used to derive: Overhead share of energy by facility class; PUE build-up.
Subsystem | Legacy/small enterprise (PUE about 1.8–2.0) | Typical enterprise/colo (PUE about 1.5–1.6) | Hyperscale cloud (PUE about 1.1–1.2) | AI liquid-cooled (PUE about 1.1–1.3)
IT load (servers, storage, network) | 50–55% | 62–67% | 83–91% | 77–90%
Cooling (chillers, CRAH/CRAC, pumps, towers, fans) | 30–40% | 25–30% | 5–10% | 7–15% (CDUs, pumps, dry coolers, residual air)
Power conversion and distribution losses (UPS, transformers, PDUs) | 8–12% | 6–8% | 2–5% | 3–6%
Lighting and other (security, offices, humidification) | 2–5% | 1–3% | about 1% | about 1%
R2-T02 Server power split: conventional CPU vs AI accelerated
Source: Report 2 (full research report) · Section 1: Anatomy of Data Centre Consumption › 1.2 Inside the IT load: CPUs, GPUs, memory, storage and networking
Note: Applying the IEA shares to IT load alone, a typical facility's IT power splits about 85% servers, about 7% storage and about 7% networking. Within a server, the split depends on the class:
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 2 text on IT-load anatomy (reference).
Used to derive: Share of rack power going to accelerators.
Component | Conventional CPU server (indicative) | AI accelerated server/rack
CPUs | about 40–55% of server power | about 10–15% (host CPUs, e.g. Grace)
GPUs/accelerators | 0% (or a small inference card) | about 60–75% (e.g. 72 × B200 at about 1.0–1.2 kW = about 72–86 kW of a 120 kW NVL72 rack)
Memory (DRAM/HBM) | about 15–25% | HBM is counted in the GPU package; host DRAM is a few %
Local storage (SSD/HDD) | about 5–10% | a few %
Fans, PSU losses, NICs | about 10–20% | Switch trays (NVLink), NICs/DPUs and PSU losses about 10–15%; fans are minimal with liquid cooling
R2-T03 Efficiency metrics: PUE, WUE, CUE and ERE
Source: Report 2 (full research report) · Section 1: Anatomy of Data Centre Consumption › 1.3 Efficiency metrics: PUE, WUE, CUE and ERE
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 2 and Ch 8 metric definitions; Key numbers (PUE 1.54, Google 1.09, MeitY <1.35).
Used to derive: PUE and WUE benchmarks for calculators.
Metric | Definition | Benchmarks
PUE (Power Usage Effectiveness) | Total facility energy ÷ IT energy | Uptime 2025 global weighted average 1.54 (1.58 in 2023, 1.56 in 2024). Facilities built in the last five years: 1.48. Sites over 20 MW: about 1.44. Many new high-latitude sites: 1.3 or better. Google fleet: 1.09 (2025). MeitY AI-cloud tenders in India require below 1.35.
WUE (Water Usage Effectiveness) | Site water (L) ÷ IT energy (kWh) | Microsoft FY24: 0.30 L/kWh, down 39% from 0.49 in 2021. Microsoft's regional values range from about 1.52 (Arizona) to 0.02 (Singapore), as reported secondhand.
CUE (Carbon Usage Effectiveness) | kgCO₂e ÷ IT kWh | Determined mainly by the grid mix and whether emissions are counted location-based or market-based
ERE (Energy Reuse Effectiveness) | (Total energy − reused energy) ÷ IT energy | Can fall below 1.0 with district-heat export, which matters for liquid-cooled AI halls producing 40–60 °C return water
R2-T04 Water per AI query: a contested range
Source: Report 2 (full research report) · Section 1: Anatomy of Data Centre Consumption › 1.4 Water consumption: direct and indirect
Note: Per-AI-query water: a contested range.
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 6 and Ch 12 "Water per AI prompt" charts.
Used to derive: Water per prompt with different boundaries.
Estimate | Water per query | Scope
UC Riverside, "Making AI Less Thirsty" (Li, Yang, Islam, Ren) | 500 mL per about 10–50 medium GPT-3 responses (about 10–50 mL each); GPT-3 training about 5.4 million L total, of which 700,000 L on site | Scope 1 + 2, GPT-3-era hardware, Microsoft US data centres
Google Gemini (May 2025) | 0.26 mL (0.15 mL under a narrower method) | On-site cooling only
OpenAI (Altman, June 2025) | about 0.32 mL | Unspecified, likely on-site
Mistral Le Chat LCA | about 45 mL per 400-token response | Full lifecycle
R2-T05 US data-centre electricity (LBNL 2024)
Source: Report 2 (full research report) · Section 1: Anatomy of Data Centre Consumption › 1.6 Global and regional electricity consumption
Note: LBNL 2024 *United States Data Center Energy Usage Report* (December 2024):
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 2 context text (reference only).
Used to derive: US growth path as a comparison for India.
Year | US data-centre electricity | Share of US electricity
2014 | 58 TWh | —
2018 | 76 TWh | 1.9%
2023 | 176 TWh | 4.4%
2028 (scenarios) | 325–580 TWh | 6.7–12.0%
R2-T06 Energy per workload
Source: Report 2 (full research report) · Section 1: Anatomy of Data Centre Consumption › 1.7 Energy per workload
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 2 "Energy per workload" table.
Used to derive: Energy per query/training run; continuous MW for inference.
Workload | Energy | Source/notes
Google web search | about 0.3 Wh | Google's oft-cited 2009 figure; likely lower today
Median Gemini Apps text prompt | 0.24 Wh (0.10 Wh active-chip-only), 0.03 gCO₂e | Google, May 2025; 33× lower energy and 44× lower carbon than May 2024. Not independently verified, and prompt length is undisclosed.
ChatGPT average query | about 0.34 Wh | Sam Altman, June 2025; no methodology
GPT-4o typical query (500 output tokens) | about 0.3 Wh | Epoch AI, February 2025 (replacing the 2023 figure of about 3 Wh)
Long-input query (10k / 100k tokens) | about 2.5 Wh / about 40 Wh | Epoch AI
Reasoning/agentic queries | several to tens of Wh | Third-party benchmarks; high uncertainty
R2-T07 Master comparison: AI vs conventional data centres
Source: Report 2 (full research report) · Section 2: AI Data Centre vs Conventional Data Centre › 2.1 Master comparison table
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 2 "Conventional vs AI" comparison table.
Used to derive: Design differences that drive cooling, power and capex choices.
Attribute | Conventional (enterprise/colo/cloud) | AI data centre (training/inference)
Primary workloads | Web, databases, ERP, storage, virtualised and cloud VMs, streaming | Large-model training (synchronous, weeks to months); inference (latency-sensitive, bursty); fine-tuning
Compute | x86/Arm CPU servers, about 300–1,000 W per server | GPUs/TPUs/ASICs: H100 700 W; B200 1,000–1,200 W; B300 about 1.4 kW; 8-GPU HGX node about 5.6–10 kW
Rack density | about 5–15 kW (Uptime: few above 30 kW; average about 7–8 kW) | about 40 kW (H100 air-cooled) → 120–132 kW (GB200 NVL72) → 135–142 kW (GB300) → about 190–230 kW (Vera Rubin, 2026) → about 600 kW to 1 MW (Kyber, from 2027)
Cooling | Air (CRAH/CRAC, hot/cold aisle containment), chillers, evaporative towers | Direct-to-chip liquid (CDUs, facility water loops), rear-door heat exchangers, immersion; residual air about 10–15%
Power distribution | 400/415 V AC to rack, 12 V server PSUs, centralised UPS | 415/480 V AC with 54 VDC busbars and power shelves now; 800 VDC from about 2027; BESS for smoothing; on-site gas generation and nuclear PPAs
Networking | North–south dominant; 10–100 GbE; leaf–spine | East–west dominant; NVLink scale-up (72 → 576 GPUs); InfiniBand or Ultra Ethernet scale-out at 400–800G per GPU; optics-heavy; many times more fibre
Facility | 1–50 MW (the IEA treats 25 MW as conventional); raised floors | 100 MW to multi-GW campuses; slab floors with rack positions over 1.3 t; taller halls for overhead busways and piping
Siting | Latency-first, close to users and internet exchanges | Power-first for training (cheap, available GW); metro or edge for inference
Capex per MW | JLL shell and core about $11.3m/MW (2026 global average). India: INR 50–55 crore/MW (SBI) | Plus up to $25m/MW tenant AI fit-out (JLL), before GPUs. India: up to INR 75 crore/MW (SBI)
Reliability | Tier III/IV, 2N power, concurrent maintainability | Training: increasingly N+1 or Tier II/III-like, relying on checkpoints. Inference: Tier III+
Load profile | Flat, diurnal and variable; low utilisation | Training: sustained near-peak with sub-second synchronised swings. Inference: bursty
PUE | 1.5–1.6 average; 1.1–1.2 hyperscale | 1.1–1.3 achievable with liquid cooling; IT share about 75% or more
Water | Evaporative towers can mean WUE above 1 L/kWh | Closed-loop liquid cooling can reach near-zero WUE but may raise PUE; indirect water rises with load
Obsolescence | Hardware refreshed every 5–7 years; shell lasts 15–20+ years | GPU generations every year; economic life about 3–6 years (contested); shells risk stranding on density
Grid and regulatory exposure | Moderate | High: NERC Level 3 alert, large-load tariffs, interconnection queues, local opposition
R2-T08 Compute hardware and power
Source: Report 2 (full research report) · Section 2: AI Data Centre vs Conventional Data Centre › 2.3 Compute hardware and power
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 2 "Rack density and chip power" chart and Rack inspector.
Used to derive: kW per rack and per GPU used in sizing.
Platform | Power | Notes
Nvidia H100 SXM | 700 W | 8-GPU node about 5.6 kW (GPUs) to about 10 kW (node); racks about 30–40 kW
Nvidia B200 | 1,000 W (HGX) to 1,200 W (NVL72) | Air-cooled HGX B200 racks about 60 kW
GB200 NVL72 | about 120 kW (Nvidia); 132 kW nominal (HPE: 115 kW liquid + 17 kW air); peak electrical design power about 192 kW | 72 GPUs + 36 Grace CPUs; about 1.36 t; eight 33 kW power shelves
GB300 NVL72 | 135 kW (Nvidia Mission Control); 142 kW (Nvidia/Vertiv reference) | B300 at about 1.4 kW per GPU
Vera Rubin NVL144 (2026) | about 190–230 kW (industry reports) | Transitional AC/54 VDC or 800 VDC input
Rubin Ultra / Kyber (2027+) | about 600 kW (GTC 2025), designed for up to 1 MW racks | Kyber redesigned at GTC 2026; SemiAnalysis reports a possible slip to 2028
Google TPU (Trillium, Ironwood); AWS Trainium | Lower per chip than Nvidia's flagships; liquid-cooled pods at scale | Google says Ironwood is 30× more efficient than its first TPU
Conventional CPU server | about 300–1,000 W | 2-socket x86; 5–15 kW per rack
R2-T09 Training vs inference data centres
Source: Report 2 (full research report) · Section 2: AI Data Centre vs Conventional Data Centre › 2.15 Inference versus training data centres
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 2 "Training vs inference sites" table.
Used to derive: Siting rule: train near power, serve inference near users.
| Training DC | Inference DC
Location | Power-rich, remote, cheap land | Metro or edge, near users (latency of tens of ms)
Size | 300 MW to 5 GW single campus | 10–200 MW, distributed
Network | Massive internal fabric; little external | Strong external connectivity and peering
Redundancy | Lower (checkpointing) | Higher (Tier III+)
Hardware | Newest flagship GPUs | Mix, including older GPUs, inference ASICs and L40S-class cards
Trend | Fewer, larger campuses | Growth of metro or edge AI zones and retrofitted colocation

## R3
Report 3 · Cooling
15 tables. Source line under each title; "Note" gives the context sentence from the report.
R3-T01 Accelerator power trend per GPU
Source: Report 3 (full research report) · 1. Fundamentals › 1.1 Why cooling is needed
Note: Accelerator power trend (per GPU):
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 3 cooling chain and GPU power figures.
Used to derive: Why air cooling stops working as GPUs pass ~1 kW.
GPU | Year | Max TDP | Cooling implication
Nvidia H100 SXM | 2022–23 | 700 W | Air-coolable (HGX); DLC optional
Nvidia B200 | 2024–25 | 1,000 W (up to ~1,200 W in GB200 configurations) | Air HGX options exist; GB200 NVL72 rack is liquid
Nvidia B300 (Blackwell Ultra) | H2 2025 | 1,400 W (liquid bin); 1,100 W air bin | GB300 NVL72 requires DLC; DGX B300 has an air-cooled 14.5 kW variant
Nvidia Rubin (Vera Rubin NVL72/NVL144) | H2 2026 | ~1,800–2,300 W (industry estimates; not formally confirmed) | 100% liquid; 45°C inlet water
Rubin Ultra (Kyber NVL576) | H2 2027 | — | ~600 kW per rack, 100% liquid, no fans, 800 VDC
Leading GPUs (Dell'Oro projection) | 2029 | >4,000 W | Two-phase or embedded cooling likely needed
R3-T02 Heat transfer properties of cooling fluids
Source: Report 3 (full research report) · 1. Fundamentals › 1.2 Heat transfer properties: why liquid wins
Note: Heat removed is Q = ṁ·cp·ΔT. What matters is how much heat a given volume of fluid can carry per degree of temperature rise. The values below are standard engineering values at about 25°C.
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 3 "Why liquid wins" chart.
Used to derive: Flow needed to move heat with air vs water.
Fluid | Specific heat (kJ/kg·K) | Density (kg/m³) | Volumetric heat capacity (kJ/m³·K) | Relative to air | Notes
Air | ~1.0 | ~1.2 | ~1.2 | 1× | Low thermal conductivity (~0.026 W/m·K)
Water | ~4.18 | ~1,000 | ~4,180 | ~3,500× | Conductivity ~0.6 W/m·K; conductive and corrosive, so loops must be sealed and treated
PG25 (25% propylene glycol) | ~3.9 | ~1,020 | ~4,000 | ~3,300× | Standard technology cooling system (TCS) fluid for cold plates; biocide and freeze protection
Synthetic or hydrocarbon dielectric oil (single-phase immersion) | ~1.9–2.3 | ~800–850 | ~1,600–1,900 | ~1,400× | Higher viscosity means slower convection
Fluorocarbon or HFO dielectric (two-phase) | ~1.1–1.3 | ~1,400–1,700 | ~1,700–2,000 (sensible) | — | Boiling absorbs latent heat (~90–140 kJ/kg); heat transfer coefficient 5–10× single-phase
R3-T03 ASHRAE air-cooled classes (IT inlet air)
Source: Report 3 (full research report) · 1. Fundamentals › 1.3 ASHRAE TC 9.9 thermal guidelines (5th edition, 2021)
Note: Air-cooled classes (IT inlet air):
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 3 reference (ASHRAE classes).
Used to derive: Allowable inlet temperatures; economiser hours.
Class | Recommended | Allowable dry-bulb | Typical use
A1 | 18–27°C | 15–32°C | Enterprise and mission-critical
A2 | 18–27°C | 10–35°C | Volume servers
A3 | 18–27°C | 5–40°C | Extended-range, chillerless designs
A4 | 18–27°C | 5–45°C | Extreme economisation
H1 (high-density) | 18–22°C | 15–25°C | Tightly integrated, high-power air-cooled systems that cannot meet A2
R3-T04 ASHRAE liquid-cooling W classes
Source: Report 3 (full research report) · 1. Fundamentals › 1.3 ASHRAE TC 9.9 thermal guidelines (5th edition, 2021)
Note: Liquid-cooling W classes (facility water supply temperature): the 5th edition renamed W1–W5 by their upper temperature limit. All classes share a 2°C lower bound.
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 3 "Warm-water explorer" (W32–W45 setpoints).
Used to derive: Which heat rejection works at a given facility water temperature.
Class (old name) | Facility water supply | Typical heat rejection
W17 (W1) | 2–17°C | Chillers, with economiser assist
W27 (W2) | 2–27°C | Chillers with large economiser share
W32 (W3) | 2–32°C | Cooling towers or dry coolers; chillers for trim
W40 (new) | 2–40°C | Mostly chiller-free
W45 (W4) | 2–45°C | "Typically operated without chillers": dry coolers year-round in most climates
W+ (W5) | >45°C | Heat reuse and district heating
R3-T05 Key cooling metrics
Source: Report 3 (full research report) · 1. Fundamentals › 1.5 Key metrics
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 3 and simulator PUE/WUE reasoning (reference).
Used to derive: Typical PUE/WUE ranges for calculators.
Metric | Definition | Typical values / notes
PUE | Total facility energy ÷ IT energy | Legacy air: 1.5–1.8; good modern air with economisers: 1.2–1.4; DLC: 1.05–1.2; immersion: ~1.03–1.08 (vendor-reported). The SBI report says cooling "can account for up to 40 percent of total energy usage" in Indian facilities.
pPUE (partial PUE) | (IT + subsystem energy) ÷ IT energy for one subsystem | A cooling pPUE of 1.05–1.15 is excellent
WUE | Annual site water (L) ÷ IT energy (kWh) | 0 (dry) to more than 2 L/kWh (fully evaporative); US average 1.8 L/kWh (LBNL, Shehabi et al., 2016)
kW per rack | Cooling capacity delivered per rack | Uptime 2025: average modal density ~9 kW (up from 8.3 kW); AI racks 40–230 kW, heading to 600 kW+
ΔT | Temperature rise across a coil, server or loop | Air: 10–20 K; TCS: ~10 K. Bigger ΔT means less flow and less pump or fan energy.
Approach temperature | Gap between leaving fluid and its heat sink | Towers: 3–5 K over wet-bulb; dry coolers: 5–10 K over dry-bulb; CDU HX: 2–4 K
Chiller COP / kW per ton | Cooling output ÷ electrical input; 1 ton = 3.517 kW | Water-cooled centrifugal: ~0.5–0.6 kW/ton (COP ~6–7); air-cooled screw: ~1.0–1.2 kW/ton (COP ~3)
IPLV / NPLV | Weighted part-load efficiency (100/75/50/25% load) | Matters because data centre chillers rarely run at full load. India's ECBC data-centre guidance cites, for example, centrifugal chillers ≥1,580 kWr at COP 6.3 and IPLV 7.0.
R3-T06 Chiller types
Source: Report 3 (full research report) · 3. Chilled-water plants and heat rejection › 3.1 Chiller types
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Reference only (chiller choice in Ch 3 text).
Used to derive: Chiller efficiency assumptions.
Type | Compressor | Size range | Typical full-load efficiency | Notes
Air-cooled scroll | Scroll | 50–500 kW | ~1.1–1.3 kW/ton | Small sites, edge
Air-cooled screw | Screw | 300–2,000 kW | ~1.0–1.2 kW/ton | No tower water; often with integrated free-cooling coils
Water-cooled screw | Screw | 500–3,500 kW | ~0.6–0.7 kW/ton | Needs towers
Water-cooled centrifugal | Centrifugal | 1,000–10,000+ kW | ~0.5–0.6 kW/ton | Best at scale
Magnetic-bearing centrifugal (e.g., Danfoss Turbocor compressors) | Oil-free, variable speed | 300–5,000 kW | Full load ~0.55; IPLV can approach ~0.3–0.35 kW/ton | Excellent part-load efficiency and low maintenance
Free-cooling chillers | Any, plus integrated dry coils | — | Compressors off when ambient is ~8–10 K below return water | Very effective at higher water temperatures
R3-T07 Liquid cooling comparison
Source: Report 3 (full research report) · 4. Liquid cooling types › 4.7 Liquid cooling comparison
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 3 "Liquid cooling compared" table.
Used to derive: Density, PUE and maturity per liquid technology.
Attribute | Single-phase DLC | Two-phase DLC | Single-phase immersion | Two-phase immersion | RDHx (active)
Practical rack density | 50–250 kW+ (with air assist) | 100–300 kW+ | 100–250 kW per tank | 200 kW+ per tank | 40–75 kW
Heat to liquid | 70–98% | 70–95% | ~100% | ~100% | 100% at the door (air-side)
Facility water class | W32–W45 | W32–W45 | W32–W45 | W32–W45 | W17–W27 (needs colder water)
PUE (reported range) | 1.05–1.20 | 1.04–1.15 | 1.03–1.08 | 1.01–1.05 | 1.15–1.35
Fluid | PG25 / water (cheap) | Dielectric refrigerant ($$) | Hydrocarbon or synthetic oil ($–$$) | Fluorocarbon or HFO ($$$) | Water
Serviceability | Server-like; QDs | Server-like; pressurised | Lift-out, drain | Sealed tank | Easy
Weight / floor | Heavy racks (1.5–3 t) | Heavy racks | Heavy tanks, low floor density | Heavy tanks | Moderate
OEM support / warranty | Mainstream (Nvidia reference) | Emerging | Improving; check per OEM | Limited | Mainstream
Maturity (2026) | Mainstream for AI | Early commercial | Niche but proven | Niche; PFAS risk | Mature
OCP / standards | OCP ACS cold plate, CDU, UQD specs; ORv3 | OCP ACS two-phase workstream | OCP ACS immersion specs | OCP ACS immersion | OCP Door HX workstream
R3-T08 Natural and alternative cooling
Source: Report 3 (full research report) · 5. Natural and alternative cooling
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 3 text on natural cooling; Ch 12 seawater option.
Used to derive: Relevance of seawater and free cooling for India.
Approach | Flagship examples | How it works | Relevance to India
Climate free cooling | Nordic sites (Meta Luleå, many in Finland, Norway, Iceland) | Cool, dry ambient air: indirect or direct economisers for most of the year. Cool-climate adiabatic sites "may rely on free cooling for 90% to 95% of the year." | Limited. Only hill or high-altitude sites and winter months.
Seawater cooling | Google Hamina, Finland (former paper mill using Baltic seawater) | Cold seawater through titanium HX to the facility loop | Tropical surface seawater is ~27–31°C, too warm for chilled water but usable for heat rejection at W32–W45. Andhra Pradesh's data-centre policy proposes seawater cooling. Indian coastal thermal plants (NTPC Simhadri, Hinduja Vizag) already use seawater for condenser cooling.
Deep lake / deep water | Enwave Deep Lake Water Cooling, Toronto (Lake Ontario at ~4°C) | Cold deep water through district cooling | No equivalent cold deep lakes near Indian metros
Groundwater / geothermal | Various European aquifer thermal energy storage sites | Aquifer as heat sink or seasonal storage | Restricted. Indian groundwater is overdrawn.
Underwater | Microsoft Project Natick (Orkney, 2018–2020); China's commercial underwater data centre off Hainan and a reported offshore-wind-linked project near Shanghai | Sealed pressure vessel cooled by surrounding seawater | Microsoft says the Natick servers "showed a failure rate of 1/8th that of our land-based control group" (vessel retrieved July 2020), but Microsoft confirmed in 2024 that the project is no longer active. China's projects are reported commercial pilots, not independently verified here. A curiosity for India.
Heat reuse / district heating | Stockholm Data Parks; Meta Odense (Denmark) | Heat pumps lift 25–45°C waste heat to 60–80°C district heating | Low heating demand in India. Better candidates are absorption chillers, desalination pre-heat, or industrial process heat.
R3-T09 Liquid-cooling market size and forecasts
Source: Report 3 (full research report) · 6. Market and adoption › 6.1 Market size and forecasts (2024–2031)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 3 "Liquid-cooling market" chart; Ch 11 Bass diffusion analogue.
Used to derive: Adoption speed for liquid cooling.
Source (date) | Metric | Figure
Dell'Oro (Jan 2026) | Global DC liquid cooling, manufacturer revenue | ~$3 billion in 2025 (≈2× 2024), ~$7 billion by 2029
Dell'Oro (Aug 2025) | Direct liquid cooling | $1.1 billion (2024) to $5.8 billion (2029); DLC grew 156% year on year in 2Q 2025
Dell'Oro (2026) | DLC 2030 | ~$8 billion by 2030
Dell'Oro (Aug 2025, 2026 update) | Data centre physical infrastructure (DCPI) | $63.1 billion by 2029 (15% CAGR); >$80 billion by 2030. Thermal management CAGR 19–20%.
MarketsandMarkets | India DC liquid cooling | $113.0 million (2026) to $789.9 million (2031), ~32% CAGR
Other analyst estimates (secondary) | Global "liquid cooling" (broader definitions) | ~$5.5 billion (2025) to ~$15.8 billion (2030)
R3-T10 Cooling vendor landscape and consolidation
Source: Report 3 (full research report) · 6. Market and adoption › 6.4 Vendor landscape and consolidation (2024–2026)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 3 "Who bought whom" bars.
Used to derive: Supply-chain concentration risk.
Company | Position / recent moves
Vertiv | Dell'Oro names it the liquid cooling market leader. Acquired CoolTera (CDUs, UK, announced Dec 2023) and agreed to buy PurgeRite (~$1 billion, Nov 2025; fluid services). Vertiv did not buy CoolIT.
Ecolab to buy CoolIT | Announced 20 Mar 2026: ~$4.75 billion cash from KKR and Mubadala, about 29× next-12-month EBITDA; CoolIT expected to generate ~$550 million in sales. Closing reported in early July 2026.
Eaton to buy Boyd Thermal | $9.5 billion (Nov 2025; 22.5× 2026E EBITDA). Boyd forecast $1.7 billion of 2026 sales, $1.5 billion of it liquid cooling. Closing reported in March 2026.
Schneider Electric to buy Motivair | $850 million for a controlling stake (2024). Motivair liquid cooling factory opened in Bengaluru (~March 2026), its third globally.
Trane Technologies to buy LiquidStack | Announced 10 Feb 2026, closed 3 Mar 2026. Brings DLC CDUs and single- and two-phase immersion.
nVent, CoolIT, Boyd | Named by Dell'Oro as holding strong DLC share
Others | Asetek, Submer, GRC, Iceotope, Stulz, Rittal, Carrier, Johnson Controls (Silent-Aire), Daikin, Danfoss, Munters, Airedale, Delta, and Taiwanese cold-plate makers
Indian players | Mostly integrators and assemblers: Blue Star, Voltas and Kirloskar (chillers), plus local system integrators. Global vendors manufacture locally (Section 9.5).
R3-T11 Water–energy trade-off by heat-rejection type
Source: Report 3 (full research report) · 7. Water–energy trade-offs › 7.1 The core trade
Note: Evaporating 1 kg of water absorbs ~2,400 kJ, so towers can reject heat close to the wet-bulb temperature. Dry systems can only approach the dry-bulb temperature, which is often 8–15 K higher in hot-dry climates.
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 3 heat-rejection table; simulator WUE functions; Ch 12 power-vs-water chart.
Used to derive: Water vs energy trade-off per design.
Heat rejection | On-site WUE (L/kWh IT) | Energy effect | Best climate
Open cooling tower + water-cooled chiller | ~1.4–2.5 typical; 2–4 for traditional evaporative systems | Lowest chiller energy; evaporative cooling "reduces the peak cooling power demand by 25–35% in the summer compared with dry cooling" | Hot-dry with ample (ideally non-potable) water
Direct / indirect evaporative air cooling | ~0.2–1.5 (seasonal) | Very low energy when humidity is low | Hot-dry (Delhi and Hyderabad pre-monsoon, Bengaluru dry season)
Adiabatic dry cooler | ~0.1–0.5 | Wets coils only on peak days | Most climates; India's best compromise
Hybrid / thermosyphon | ~0.5–0.7 (NREL: 1.27 to 0.70) | Near-evaporative energy, about half the water | Mixed
Dry cooler + air-cooled chiller | ~0 | Cooling energy 5–15% higher than evaporative (more in hot climates); air-cooled chillers can use 2–3× the electricity of evaporative-cooled ones at peak | Water-scarce sites
DLC at W40–W45 + dry cooler | ~0 to <0.1 | Small penalty, since 45°C water can be dry-cooled even at 35–40°C ambient | Almost anywhere, including India
Seawater once-through | ~0 freshwater | Pumping energy only; marine permitting and thermal discharge limits | Coastal
R3-T12 Cooling capex by approach (indicative)
Source: Report 3 (full research report) · 8. Cost › 8.1 Capex by cooling approach (indicative, 2025–26)
Data basis: Proxy / estimate
Used in atlas: Simulator cooling capex adder (₹0–3 cr/MW).
Used to derive: Capex premium for liquid cooling.
Approach | Cooling-system capex | Notes
Traditional air (CRAH + chillers + containment) | ~$1.5–2 million per MW of IT | Cannot serve 100 kW+ racks
Advanced air with RDHx | ~$1,800–3,200 per kW | Bridge for 30–60 kW racks
Single-phase DLC (CDU, manifolds, piping, plus heat rejection) | ~$3–4 million per MW all-in cooling (some sources: $3,500–5,000 per kW). The CDU, manifold and cold-plate subset is ~$300–650 per kW. | CDUs ~$75,000–150,000 per 500 kW; cold plates and manifolds ~$5,000–10,000 per server; ~$50,000 per NVL72 rack
Single-phase immersion | ~$1 million per MW for tanks and fluid systems (versus ~$650,000 for comparable DLC hardware); $2.5–3.5 million per MW all-in (vendor-adjacent estimates) | Some vendor-sponsored TCO studies claim lower total capex than air at high density; treat with caution
Retrofit an air hall to liquid | ~$2–3 million per MW of cooling capacity | 12–18-month lead times for raised-floor facilities
R3-T13 Indian city climates and free-cooling outlook
Source: Report 3 (full research report) · 9. The Indian perspective › 9.1 Climate challenge
Note: India's problem is heat plus humidity. High wet-bulb temperatures limit evaporative cooling, high dry-bulb temperatures limit dry coolers, and dust, pollution and monsoon humidity largely rule out direct fresh-air cooling.
Data basis: Proxy / estimate
Used in atlas: Ch 3 city cards; simulator design temperatures; Ch 4 day model.
Used to derive: Free-cooling potential and PUE by city.
City | Climate character | Free-cooling outlook | Indicative peak wet-bulb*
Mumbai / Navi Mumbai | Hot-humid coastal, monsoon | Poor for air-side; one estimate gives ~28% economiser hours at conventional setpoints | ~28°C design; monsoon peaks reportedly 30–32°C
Chennai | Hot-humid coastal, severe water stress | Poor for air-side; good for W40–W45 dry cooling | ~28–29°C
Delhi NCR / Noida | Composite: very hot-dry summer (>45°C dry-bulb), humid monsoon, cool winter | Good winter economisation (Dec wet-bulb 3–8°C); summer is the worst case for dry coolers | ~29°C
Bengaluru | Moderate, elevated (~900 m) | Best in India; one estimate gives ~71% free-cooling hours at a 35°C dry-cooler setpoint | ~23°C
Hyderabad | Hot semi-arid | Good for indirect evaporative cooling much of the year; hot April–May | ~25–26°C
Visakhapatnam | Hot-humid coastal | Seawater heat rejection possible; water-stress controversy | ~28°C
R3-T14 Indian operators: liquid-cooling deployments
Source: Report 3 (full research report) · 9. The Indian perspective › 9.2 Indian operators and liquid cooling deployments
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 3 "Indian deployments" list.
Used to derive: State of liquid cooling in India.
Operator | Liquid cooling status (sourced)
Sify | First in India to be certified for liquid cooling under Nvidia's DGX-Ready programme (Rabale, Navi Mumbai; Sept 2024), specified "to support 130 KW/rack." Chennai 02 (Siruseri) and Noida 02 certified for "up to 200 KW/rack" (May 2025).
Yotta | NM1 (Navi Mumbai) hosted ~16,000 H100/GH200 GPUs by mid-2025 (secondary source). Yotta says RDHx supports "50–60 kW" and DLC "up to 80 kW per rack." It has announced plans for 40,000 Vera Rubin GPUs at D4 Greater Noida (120 MW) and GB300 at NM2. These are plans, not commissioned capacity.
CtrlS | Marketing claims of AI racks up to 70 kW (RDHx, DLC, immersion) and immersion "up to 250kW per rack." Plans for more than 4 GW of AI-ready capacity. No independently verified rack-level DLC deployment details were found.
NTT DATA India | NAV1 Mahape: 4.8 MW of immersion plus direct contact liquid cooling (2023).
Nxtra (Airtel) | ~300 MW capacity (March 2026); reported "high-density racks of up to 130 kW using air and liquid cooling" (secondary).
STT GDC India | Expanding AI-ready capacity; no published liquid-cooling rack density found.
Google / AdaniConneX / Nxtra (Vizag) | 1 GW AI hub; Google says air-cooled (dry) heat rejection; under legal and community challenge over water.
R3-T15 Recommended cooling for India by use case
Source: Report 3 (full research report) · 9. The Indian perspective › 9.6 Recommendations for India: what to use where
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 3 "What to use where in India" table.
Used to derive: Recommended design per use case and city.
Use case | Recommended cooling | Heat rejection | Target PUE / WUE
AI training / inference (≥40 kW per rack), any city | Single-phase DLC (W32–W45), with RDHx or fan-wall for the residual 10–25% | Dry coolers with adiabatic assist on peak days; magnetic-bearing chillers only for trim and resilience | PUE 1.15–1.25; WUE <0.2
AI halls in coastal Mumbai, Chennai, Vizag (hyperscale) | DLC as above | Seawater or treated-sewage-water heat rejection where permitted; otherwise adiabatic dry coolers | PUE ~1.2; freshwater WUE ~0
Cloud / enterprise (8–20 kW per rack), Bengaluru, Hyderabad, Pune | Hot aisle containment, fan walls or CRAH | Indirect evaporative coolers or air-cooled free-cooling chillers; recycled water if evaporative | PUE 1.3–1.4; WUE 0.2–0.8
Cloud / enterprise in Mumbai and Chennai | Hot aisle containment, CRAH, higher chilled-water setpoints (18–20°C) | Water-cooled magnetic-bearing chillers on recycled water, or air-cooled free-cooling chillers in water-stressed zones | PUE 1.35–1.5
Delhi NCR | Hot aisle containment plus economiser for winter; DLC for AI | Hybrid: dry/adiabatic in winter and monsoon, evaporative trim in May–June using recycled water | PUE 1.25–1.4
Edge / telecom / dusty sites | Sealed DX (R-32 / low-GWP) or single-phase immersion micro-pods | Dry | —
Retrofits of existing Indian air halls for GPUs | L2A CDUs (AWS IRHX / Meta AALC style) or active RDHx up to ~50–70 kW; full L2L DLC needs facility water risers | Existing chilled water | —

## R4
Report 4 · Bengaluru water and power
8 tables. Source line under each title; "Note" gives the context sentence from the report.
R4-T01 Assumptions for the three Bengaluru cases
Source: Report 4 (full research report) · 1. Assumptions
Data basis: Proxy / estimate
Used in atlas: Ch 4 campus calculator presets; simulator defaults.
Used to derive: Input assumptions for the three Bengaluru cases.
Parameter | Case A: Colo/enterprise | Case B: Hyperscale/cloud | Case C: AI campus
Design IT load | 20 MW | 50 MW | 100 MW
Cooling | Water-cooled chillers + cooling towers (with water-side economiser) | B1: chillers + cooling towers; B2: adiabatic/hybrid dry coolers | DLC (~80% to liquid) + dry coolers with adiabatic assist
Annual PUE (central / range) | 1.45 / 1.30–1.60 | 1.35 / 1.25–1.45 | 1.20 / 1.15–1.25
Average utilisation of design IT | 70% / 60–85% | 75% / 65–85% | 80% / 70–90%
Design-day PUE (for contract demand) | 1.6 | 1.5 | 1.3
On-site WUE (L/kWh IT) | 1.8 / 1.5–2.0 | B1: 1.6; B2: 0.4 | Dry 0.05; adiabatic 0.2; (evaporative alt. 1.6)
Staff on site | ~150 | ~300 | ~300
Grid water intensity | 1.5 L/kWh (range 1.0–2.5) | same | same
R4-T02 Power calculations by case
Source: Report 4 (full research report) · 2. Power calculations
Note: Contract demand (MVA) ≈ Design IT × design-day PUE ÷ power factor (0.95), plus ~3–5% for offices and losses
Data basis: Calculated (model output)
Used in atlas: Ch 4 calculator outputs (MU, MVA, homes, % of state demand); Key numbers (841 MU, 140 MVA).
Used to derive: Energy, contract demand and share of Karnataka demand per case.
| Case A (20 MW) | Case B (50 MW) | Case C (100 MW)
IT energy | 20×0.70×8,760 = 122.6 GWh | 50×0.75×8,760 = 328.5 GWh | 100×0.80×8,760 = 700.8 GWh
Facility energy (central) | 122.6×1.45 = 177.8 MU | 328.5×1.35 = 443.5 MU | 700.8×1.20 = 841.0 MU
Sensitivity range | 136.7–238.3 MU | 355.9–539.8 MU | 705.2–985.5 MU
Average draw | 20.3 MW | 50.6 MW | 96.0 MW
Design peak | 32 MW | 75 MW | 130 MW
Contract demand | ~34–35 MVA | ~80 MVA | ~140 MVA
Supply voltage (KERC norms) | 110 kV | 220 kV | 220 kV, dedicated substation, dual feed
Installed transformer capacity (2N) | ~70 MVA | ~160 MVA | ~280 MVA
Bengaluru household equivalent (1,800 kWh/yr) | ~98,800 | ~246,400 | ~467,200
Share of Karnataka energy (92,550 MU, FY25) | 0.19% | 0.48% | 0.91%
Share of BESCOM sales (~37,000 MU, est.) | 0.48% | 1.2% | 2.3%
Share of state household use (16,089 MU) | 1.1% | 2.8% | 5.2%
Share of 2026 state peak (20,094 MW) | 0.17% | 0.40% | 0.67%
Energy bill at HT-2a (Rs 6.70/kWh + Rs 365/kVA/month) | ~Rs 134 cr/yr | ~Rs 332 cr/yr | ~Rs 625 cr/yr
R4-T03 On-site water by case
Source: Report 4 (full research report) · 3. Water calculations › 3.2 On-site water by case
Note: Formula: annual on-site water (L) = IT energy (kWh) × WUE + staff × 45 L × 365 + landscaping. MLD = annual ML ÷ 365. Population equivalent = MLD × 10⁶ ÷ 135.
Data basis: Calculated (model output)
Used in atlas: Ch 4 water bars and "Water you can picture" (Ch 6).
Used to derive: On-site MLD and people-equivalent per case.
Case / cooling | Cooling water | Domestic + landscaping | Total on-site | Range | People at 135 LPCD
A (WUE 1.8) | 122.6 GWh×1.8 = 220.8 ML/yr = 0.605 MLD | ~0.02 MLD | ~0.62 MLD (226 ML/yr) | 0.43–0.82 MLD | ~4,600
B1 evaporative (1.6) | 525.6 ML/yr = 1.44 MLD | ~0.03 MLD | ~1.47 MLD | 1.1–1.9 MLD | ~10,900
B2 adiabatic (0.4) | 131.4 ML/yr = 0.36 MLD | ~0.03 MLD | ~0.39 MLD | 0.2–0.6 MLD | ~2,900
C dry/closed-loop (0.05) | 35.0 ML/yr = 0.096 MLD | ~0.03 MLD | ~0.13 MLD | 0.06–0.2 MLD | ~930
C adiabatic assist (0.2) | 140.2 ML/yr = 0.38 MLD | ~0.03 MLD | ~0.41 MLD | 0.3–0.6 MLD | ~3,050
C if built with cooling towers (1.6) | 1,121 ML/yr = 3.07 MLD | ~0.03 MLD | ~3.10 MLD | 2.6–3.6 MLD | ~23,000
R4-T04 Indirect water embedded in grid electricity
Source: Report 4 (full research report) · 3. Water calculations › 3.3 Indirect water embedded in grid electricity
Note: Using Raichur's reported actual of ~4.9 m³/MWh would push this towards 2.5. Raichur sits on the Krishna and has been shut during water shortages.
Data basis: Calculated (model output)
Used in atlas: Ch 4 power-station water bar; simulator grid water (KA 1.5 L/kWh).
Used to derive: Indirect water per case.
| Case A | Case B | Case C
Indirect water (1.5 L/kWh) | 177.8 GWh → 267 ML/yr = 0.73 MLD | 443.5 GWh → 665 ML/yr = 1.82 MLD | 841 GWh → 1,262 ML/yr = 3.46 MLD
Total footprint (on-site + indirect) | ~1.35 MLD | B1 ~3.3 / B2 ~2.2 MLD | dry ~3.6 / adiabatic ~3.9 MLD
With 100% solar/wind supply | ~0.62 MLD | B1 1.47 / B2 0.39 | 0.13–0.41
R4-T05 Comparison with other Bengaluru and Karnataka water users
Source: Report 4 (full research report) · 4. Comparison with other Bengaluru and Karnataka users
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 4 "Compared with other users" chart.
Used to derive: Data-centre water in context of other users.
User (illustrative scale) | Water (MLD) | Per-unit norm | Power (MU/yr) | Source / status
Case A, 20 MW colo | 0.62 | 1.8 L/kWh IT | 178 | This model
Case B1, 50 MW evaporative | 1.47 | 1.6 L/kWh IT | 444 | This model
Case C, 100 MW DLC | 0.13–0.41 | 0.05–0.2 L/kWh IT | 841 | This model
IT campus, 10 million sq ft (Manyata/ITPL scale, ~100,000 staff) | ~5.5–6.5 (4.5 domestic at 45 LPCD + HVAC towers) | 45 LPCD/employee | ~185 (≈200 kWh/m²/yr) | Estimate from norms
Apartment complex, 1,000 flats | ~0.61 | 135 LPCD × 4.5 persons | ~18 | Norm-based
500-bed hospital | ~0.23 | ~450 L/bed/day (NBC) | ~15–25 | Norm-based estimate
300-room luxury hotel | ~0.3 | ~1,000 L/room/day | ~10–15 | Industry-typical estimate
Large mall, ~1 million sq ft | ~0.3–0.5 | — | ~25–35 | Estimate
Brewery, 2 million hl/yr | ~1.7 | UBL: 2.93 kL/kL (FY24), 3.10 kL/kL (FY25) | ~15–20 | UBL reports; plant size illustrative
Soft-drink bottler, 1 million kL/yr | ~4–6 | ~1.5–2.2 L/L industry-typical | ~20–30 | Estimate
Toyota Kirloskar, Bidadi (capacity ~342,000 vehicles) | ~4.7 total (1.73 million m³/yr), ~89–90% recycled or rainwater | 2.94 m³/vehicle (2016-17) | 100% renewable since FY2021 | TKM disclosures
BEL (Bengaluru) | ~2 MLD of BWSSB treated water | — | — | Deccan Herald via BWSSB
18-hole golf course (dry season) | ~1.5–2.5 | ~5 mm/day on ~40–50 ha | <5 | Estimate
Garment factory (cut-make-trim), 2,000 workers | ~0.1 | Domestic-type use; wet processing 100–200 L/kg elsewhere | ~5–10 | Estimate
BMRCL Namma Metro (96 km) | Small (stations, depot washing) | — | ~65 lakh units/month in 2018-19 (~78 MU/yr); now plausibly ~200 MU; Blue Line alone projected at 152 GWh | BMRCL (2019), IISc–BMRCL study
JSW Steel Vijayanagar (12–17.5 MTPA) | 330 MLD allocated (Tungabhadra 32 MGD + Almatti 40 MGD) | ~10 m³/t on allocation basis | Captive ~860 MW plants | JSW environmental clearance filing
Raichur TPS (1,720 MW) | ~110–150 at 3.5–4.9 m³/MWh | MoEFCC norm 3.5 | Generator | CPCB / reported data
Pharma/biotech (Biocon), HAL | Not publicly disaggregated | — | — | Data gap
R4-T06 Where Bengaluru data centres get water today
Source: Report 4 (full research report) · 5. Where Bengaluru data centres get water today
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 4 "The city's water" table.
Used to derive: Sources and prices of water in Bengaluru.
Source | Status for data centres | Key facts
BWSSB Cauvery (Stages I–V) | Used for a few; poorly metered | Stages I–IV ~1,450 MLD; Stage V adds 775 MLD (commissioned Oct 2024), but connection uptake is slow (<1.2 lakh of 4 lakh targeted connections after 18 months). Cauvery allocation is capped. BWSSB industrial tariff Rs 99/kL. Five data centres receive ~129 kL/month in BWSSB records.
Groundwater/borewells | Likely the dominant source (WELL Labs view) | All Bengaluru Urban and Rural assessment units are over-exploited. Bangalore East is at 378.85% (Karnataka Dynamic Ground Water Resources report; 395.0% in IN-GRES 2025-26 data), Devanahalli at 169%, with "no net groundwater available for future use". The whole area is notified under the Karnataka Ground Water Act 2011, so every borewell needs a KGWA/BWSSB permit.
Private tankers | Back-up; unregulated | Tanker water is mostly borewell water from peri-urban villages, which moves the depletion elsewhere.
Treated wastewater (STP/tertiary) | Under-used; no mandate | BWSSB STP capacity ~1,348.5 MLD. Reuse ~825 MLD environmental and ~30 MLD commercial. K&C Valley sends 440 MLD and H-N Valley 210 MLD (secondary treated) to Kolar and Chikkaballapur. Treated water sells at Rs 10–15/kL. Apartment STPs may sell 50% of their output. BWSSB's chair has said there is no mandate for data centres to use recycled water.
Rainwater harvesting / on-site STP | Supplementary | Useful for domestic use and landscaping. Too small and seasonal for evaporative cooling.
R4-T07 Scenarios: added IT capacity vs water (75% utilisation)
Source: Report 4 (full research report) · 6. Will data centre water cause scarcity? › 6.2 Scenarios (75% utilisation; IT energy = 18,000 kWh/day per MW)
Data basis: Calculated (model output)
Used in atlas: Ch 4 "Scaling to 1 GW" chart; Key numbers (~32 MLD).
Used to derive: City-wide water impact of the 1 GW target.
Added IT capacity | Evaporative, WUE 1.8 | Adiabatic, WUE 0.4 | Dry/DLC, WUE 0.05 | Indirect (PUE 1.3, 1.5 L/kWh), outside city
100 MW | 3.2 MLD (0.11%) | 0.7 MLD (0.02%) | 0.09 MLD | 3.5 MLD
500 MW | 16.2 MLD (0.54%) | 3.6 MLD (0.12%) | 0.45 MLD | 17.6 MLD
1 GW | 32.4 MLD (1.1%) | 7.2 MLD (0.24%) | 0.9 MLD | 35.1 MLD
People equivalent, 1 GW | ~240,000 | ~53,000 | ~6,700 | ~260,000
1 GW as share of BWSSB STP capacity (1,348.5 MLD) | 2.4% (≈43 MLD RO feed) | 0.5% | ~0 | —
R4-T08 Phased roadmap for Karnataka
Source: Report 4 (full research report) · Recommendations › Phased roadmap
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 4 "Recommended roadmap" table.
Used to derive: Policy sequence for Karnataka.
Phase | Timing | Actions
1 | Q4 2026–2027 | Operational guidelines for the 2026–31 policy. Mandatory metering and disclosure. Groundwater-for-cooling ban in over-exploited taluks. Data centre water tariff. Publish hosting-capacity map.
2 | 2027–2028 | WUE ≤0.4 and PUE ≤1.3 written into consent conditions for new builds. Treated-water pipelines to Hoskote and Whitefield clusters. ≥70% renewable rule for >50 MW. BESS and demand-response contracts.
3 | 2029–2031 | Existing-fleet WUE ≤1.0 and PUE ≤1.45. Hourly renewable matching. Independent audits. Review the 1 GW target against grid and water heat-map outcomes.

## R5
Report 5 · Carbon
8 tables. Source line under each title; "Note" gives the context sentence from the report.
R5-T01 Lifecycle carbon intensity by technology
Source: Report 5 (full research report) · 1. SOURCE — What Generates the Electron › 1.1 Lifecycle carbon intensity by technology
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 5 "Lifecycle carbon by source" bars.
Used to derive: Carbon of procurement options.
Source | IPCC AR5 lifecycle median (min–max), gCO₂e/kWh | UNECE 2021 range, gCO₂e/kWh | Direct (combustion) share | India-specific note
Coal (pulverised) | 820 (740–910) | 751 (IGCC, US) – 1,095 (PC, China) | Direct 760 (670–870) | Indian subcritical units on high-ash coal: about 0.9–1.1 tCO₂/MWh at the busbar; UNECE notes a plant-by-plant global study at about 1,130 g
Oil | ~720 (secondary compilations) | — | Mostly direct | Negligible in Indian grid
Gas CCGT | 490 (410–650) | 403–513 (92–220 with CCS) | Direct 370 (350–490) | Indian gas fleet runs at low PLF; mostly peaking/balancing
Biomass (dedicated) | 230 (130–420) | — | Biogenic accounting contested | Bagasse co-gen in Karnataka/Maharashtra
Solar PV (utility) | 48 (18–180) | 8–83 | 0 direct | Upstream manufacturing mostly on coal-heavy Chinese grid
CSP | 27 (AR5) | 27–122 | 0 | Marginal in India
Geothermal | 38 (6–79) | — | Some CO₂ from geofluid | Not deployed
Hydropower | 24 (1–2,200) | 6–147 | 0 | Tropical reservoirs can emit large biogenic CH₄; upper tail is real for shallow, warm reservoirs
Wind onshore / offshore | 11 / 12 | 7.8–16 / 12–23 | 0 | Karnataka and Tamil Nadu are major onshore wind states
Nuclear | 12 (3.7–110) | 5.1–6.4 | 0 | NPCIL fleet incl. Kaiga (Karnataka)
R5-T02 Water withdrawal vs consumption by generation source
Source: Report 5 (full research report) · 1. SOURCE — What Generates the Electron › 1.2 Water: withdrawal vs consumption by source
Note: Once-through cooling withdraws a great deal but consumes relatively little. Cooling towers withdraw less but evaporate more.
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 5 "Water consumed by source" bars; grid water in calculators.
Used to derive: Indirect water per kWh by source.
Technology / cooling | Consumption, L/MWh (approx., NREL Macknick et al. 2012 medians, converted from gal/MWh) | Withdrawal, L/MWh | Comment
Coal, cooling tower | ~1,800–2,600 (US); 2,800–4,000+ actual in India | ~2,500–4,000 (US); ~4,000 India | NREL notes tower-cooled plants sit near the ~1,000 gal/MWh (~3,800 L) upper bound
Coal, once-through | ~400–1,000 | 70,000–200,000 (CSE, India) | High thermal-pollution and intake impacts
Coal/gas, dry cooling | ~0–450 (India dry-cooled coal: 450–650 L/MWh) | Low | Efficiency penalty (higher CO₂/MWh)
Nuclear, cooling tower | ~2,500–2,700 | ~4,000–5,000 | Lowest carbon, among highest water
Nuclear, once-through / seawater | ~1,000 (largely seawater) | ~100,000–170,000 | Coastal sites (Kudankulam, Tarapur) avoid freshwater stress
Gas CCGT, cooling tower | ~700–1,000 | ~1,000 | Only the steam cycle (about one-third of output) needs cooling
Gas CCGT, dry | ~10 | ~10
Solar PV | ~20–100 (panel cleaning; higher in dusty Indian conditions) | same | Robotic dry cleaning cuts this further
Wind | ~0–5 | ~0
CSP (trough, wet tower) | ~3,000–3,500 | ~3,500 | Wettest renewable
Biopower (steam, tower) | ~2,000 (operations; crop irrigation can add orders of magnitude) | —
Hydro (reservoir evaporation) | ~13,000 (China avg) to ~245,000 (Mekonnen & Hoekstra 35-plant avg); global mean ~79,000 | Not meaningful | Highly contested (see below)
R5-T03 Country grid carbon intensity
Source: Report 5 (full research report) · 3. LOCATION — Which Grid, Which Margin, Which Basin › 3.1 Country grids (operational, annual average)
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 5 "1 TWh, seven ways" chart.
Used to derive: Carbon of the same TWh on different grids.
Grid | Approx. intensity, gCO₂(e)/kWh | Source/year | 1 TWh ≈
India | 670 (2025); 708 (2024, CO₂-only) | Ember GER 2026/2025 | 0.67–0.71 MtCO₂
China | ~550 | Ember (approx.) | ~0.55 Mt
Asia average | 544 | Ember 2025 | 0.54 Mt
World | 458 (2025); 473 (2024) | Ember | 0.46 Mt
United States | ~370 | Ember (approx.) | ~0.37 Mt
EU-27 | ~210–240 | Ember (approx.) | ~0.22 Mt
France | ~30–60 | Ember/RTE (approx.) | ~0.03–0.06 Mt
Norway | ~20–30 | (approx.) | ~0.02–0.03 Mt
R5-T04 India emission-factor types: average vs marginal
Source: Report 5 (full research report) · 3. LOCATION — Which Grid, Which Margin, Which Basin › 3.3 Average vs marginal; attributional vs consequential
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 5 text on average vs marginal factors.
Used to derive: Which factor to use for reporting vs siting.
Metric | Value (India) | Use
Weighted average (WAEF), FY24-25 | 0.710 t/MWh | Location-based Scope 2; CCTS
Operating margin (OM), FY23-24 | ~0.9+ t/MWh (fossil-only) | Short-run displacement
Build margin (BM), FY23-24 | 0.552 t/MWh | What new capacity looks like
Combined margin (CM), FY23-24 | 0.757 t/MWh | Offset baselines
Short-run marginal at evening peak | ~0.95–1.1 t/MWh (est.) | Consequential impact of new load
R5-T05 Hyperscaler Scope 2: location-based vs market-based
Source: Report 5 (full research report) · 4. CARBON INTENSITY — Definitions, Trajectory and Data-Centre Metrics › 4.4 Hyperscaler disclosures: location-based vs market-based
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 5 Microsoft Scope 2 chart.
Used to derive: Gap between location- and market-based claims.
Company | Disclosure | Location-based | Market-based | Takeaway
Microsoft (2025 report, FY24) | Scope 2, tCO₂e | 4,328,916 (FY20) → 9,955,368 (FY24), +130%; +23% y/y | 456,119 → 259,090, −43% | Electricity use 10.77 → 29.83 TWh. Market-based fell while location-based more than doubled. Asia location-based Scope 2 rose from 0.91 to 2.51 Mt
Microsoft (2026 report, FY25) | Scope 2 | 12030556 | 2707428 | Market-based jump reflects dropping unbundled RECs; not comparable with earlier years
Google (2025 report, CY2024) | Data-centre electricity +27% y/y | (location-based rose with load) | Data-centre energy emissions −12% | 66% hourly CFE; ~12% in APAC; >25 clean projects (2.5 GW) came online
R5-T06 Grid-average water intensity
Source: Report 5 (full research report) · 5. WATER INTENSITY — The Grid's Hidden Water › 5.2 Grid-average water intensity
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Grid water intensity used in Ch 4–6 and simulator (1.5–2.2 L/kWh).
Used to derive: Indirect water per kWh.
Grid | Consumption intensity | Basis
India, all thermal + non-hydro RE (2014) | 2.09 L/kWh (withdrawal 15.9 L/kWh) | IRENA/WRI 2018; *excludes hydro*
India 2027–2030 projections | 1.57–1.94 L/kWh | IRENA/CEA scenarios
India, freshwater thermal only (2018) | ~1.8 L/kWh | Derived: 2.39 bn m³ ÷ ~1,300 TWh (estimate)
India incl. hydro evaporation | Several L/kWh, highly allocation-dependent | One multi-model study says hydro is about one-third of Indian power-sector water consumption
Karnataka mix (used in this series) | ~1.5 L/kWh (excl. hydro) | Estimate: ~45–50% coal at ~3.3 L/kWh + small PV cleaning
US data-centre-weighted indirect (2023) | ~4.5 L/kWh (incl. hydro evaporation) | LBNL 2024 US Data Center Energy Usage Report, as widely cited
R5-T07 Worked matrix: carbon and water per TWh by scenario
Source: Report 5 (full research report) · SYNTHESIS — "Every TWh Is Not the Same": Worked Matrix
Note: For grid cases, losses are 8% for HT supply. For on-site/adjacent supply, losses are about 3–4% (ignored below for simplicity).
Data basis: Calculated (model output)
Used in atlas: Ch 5 "1 TWh of data-centre load, seven ways" chart (carbon and water).
Used to derive: Carbon and water per TWh by supply scenario.
# | Scenario | EF used (t/MWh) | CO₂ per TWh | EWIF (L/kWh) | Water consumed per TWh | Stress weight (basin where water is lost) | Scarcity-weighted (bn L-eq)
a | Indian grid average (CEA WAEF 0.710, +8% losses) | 0.77 | ~770,000 t | 2.17 | ~2.2 bn L | 4 (mixed; ~40% of thermal in high stress) | ~8.7
b | Karnataka consumption mix (est. 0.50, +8%) | 0.54 | ~540,000 t (range 430–600k) | 1.6 | ~1.6 bn L | 4–5 (Krishna/Raichur, Ballari) | ~6.5–8
c | Marginal coal, Indian evening peak (1.0 at part load, +8%) | 1.09 | ~1,090,000 t | 3.8–4.3 (3.5–4.0 at plant) | ~3.8–4.3 bn L | 4–5 | ~15–21
d | Karnataka solar hours, grid — average basis (~0.25–0.30) / marginal basis (coal backing down, ~0.95) | 0.30 / 1.03 | ~300,000 t (avg) / ~1,000,000 t (marginal); ~0 on curtailment days | ~0.8 (avg) | ~0.8 bn L (avg) | 4–5 | ~3–4
e | 24/7 hybrid RE + BESS via group captive/open access (90% hourly CFE; lifecycle ~40 g for the RE part; 10% residual grid at 0.77) | ~0.11 lifecycle (~0.08 operational) | ~110,000 t lifecycle; 100% CFE → ~40,000 t | 0.09 RE + 0.22 residual | ~0.3 bn L | 4–5 (residual only) | ~1.2
f1 | France (nuclear-dominant grid) | 0.03–0.06 | ~30,000–60,000 t | ~1–2.5 (many plants on rivers/sea) | ~1–2.5 bn L | 2–3 (Rhône/Loire summer stress) | ~3–6
f2 | Nordic hydro (Norway) | 0.02–0.03 | ~20,000–30,000 t | 0 (run-of-river) to >10 (gross-evaporation allocation) | contested: ~0–10+ bn L | 1 | ~0–10
g | US PJM / Northern Virginia (~0.37–0.40) | 0.38 | ~380,000–420,000 t | ~2 (thermo-electric) to 4.5 (LBNL DC-weighted incl. hydro) | ~2–4.5 bn L | 2 | ~4–9
h | Gas CCGT (IPCC lifecycle 490; direct ~370) | 0.49 | ~490,000 t (direct ~370,000) | 0.75 (tower) / 0.01 (dry) | ~0.75 bn L (tower) | site-specific (2–5) | ~1.5–3.8
i | Nuclear with cooling towers | 0.006–0.012 | ~6,000–12,000 t | 2.5–2.7 | ~2.5–2.7 bn L | site-specific; inland Indian sites 4–5 | ~10–13
— | Wind only (reference) | 0.011 | ~11,000 t | ~0 | ~0 | — | ~0
— | Solar PV only (reference) | 0.048 | ~48,000 t | 0.02–0.1 | ~0.02–0.1 bn L | 4–5 | ~0.1–0.5
R5-T08 Five-factor scorecard
Source: Report 5 (full research report) · SYNTHESIS — "Every TWh Is Not the Same": Worked Matrix › Five-factor scorecard (for a site or procurement decision)
Note: Score each factor 1 (worst) to 5 (best). Weight them by your priorities; a default is carbon 30%, water 25%, source 20%, timing 15%, location 10%.
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 5 five-factor scorecard calculator.
Used to derive: Weighted score for a site or power contract.
Factor | Question | 1 (poor) | 3 | 5 (best) | Example: Bengaluru grid-only | Example: Bengaluru + 24/7 group-captive hybrid + BESS + dry cooling
Source | What physically or contractually supplies each hour? | Unbundled RECs / grid coal | Annual-matched new PPA | Additional, deliverable, hourly CFE | 2 | 5
Timing | What share of load is hourly matched? Is flexible load in solar hours? | <30% CFE, no flexibility | 50–70% CFE | >90% CFE + DR contracts | 2 | 4–5
Location | Marginal factor of grid; consumption-based state mix; network losses | Marginal coal, high losses | Mixed grid | Low-carbon margin / on-site | 2 (national coal margin) | 4
Carbon intensity | Location-based and hourly market-based tCO₂/MWh | >0.7 | 0.3–0.5 | <0.1 | 2 (0.54–0.77) | 5 (~0.08–0.11)
Water intensity | WUE_site + PUE × EWIF, scarcity-weighted | >4 L/kWh_IT in high-stress basin | 2–3 L/kWh_IT | <0.5 L/kWh_IT or non-stressed | 1–2 (4.05 L/kWh_IT, high stress) | 4–5 (~0.5 L/kWh_IT)
Weighted score |  |  |  |  | ≈1.8 / 5 | ≈4.6 / 5

## R6
Report 6 · Water impact
22 tables. Source line under each title; "Note" gives the context sentence from the report.
R6-T01 Withdrawal vs consumption: definitions by framework
Source: Report 6 (full research report) · 1. How much water? › 1.1 Withdrawal vs consumption: definitions and why both matter
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 6 framing (reference).
Used to derive: Separate withdrawal, consumption, discharge.
Framework | Withdrawal | Consumption | Other key terms
USGS | Water removed from ground or surface sources | Water evaporated, transpired, incorporated into products or otherwise removed from the immediate water environment | Return flow
GRI 303 (2018) | 303-3: all water drawn from all sources, split freshwater (≤1,000 mg/L TDS) and "other" | 303-5: withdrawal − discharge (± storage change) | 303-4 discharge by destination and treatment; all broken out for water-stressed areas
ISO 14046 (2014) | Water use | Water not returned to the drainage basin (evaporated, integrated, transferred) | Water scarcity footprint
Water Footprint Network | — | Blue: surface or groundwater consumed. Green: soil rainwater. Grey: virtual dilution volume for pollutants | —
R6-T02 Cooling water by system
Source: Report 6 (full research report) · 1. How much water? › 1.2 Cooling water
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 6 water balance and simulator WUE values.
Used to derive: Site WUE by cooling system.
System | Mechanism | Site water (L/kWh of IT energy) | Notes
Open cooling towers + water-cooled chillers | Latent heat (about 2,400 kJ/kg → about 1.5 L per kWh of heat) | 1.4–2.5 withdrawal; 1.1–1.8 consumption | Bengaluru's moderate wet-bulb suits towers; lowest PUE
Direct / indirect evaporative air handlers | Evaporation into air | 0.3–1.5 | Seasonal
Adiabatic hybrid dry coolers | Dry coils; sprays above about 28–32°C | 0.05–0.4 | Low average, high peaks
Air-cooled chillers / dry coolers | Sensible heat only | ≈0–0.05 | PUE higher by about 0.1–0.2
Closed-loop DLC + dry coolers | Warm water (35–45°C) to cold plates | 0.01–0.15 | One-time fill about 1.5–3 L/kW (often 25% propylene glycol)
Chilled-water make-up | Closed-loop losses | <0.01 | Quality matters more than volume
R6-T03 Non-cooling water uses (50 MW campus)
Source: Report 6 (full research report) · 1. How much water? › 1.3 Non-cooling water
Data basis: Proxy / estimate
Used in atlas: Ch 6 water balance (non-cooling 14.6 ML/yr).
Used to derive: Non-cooling water allowance.
Use | 50 MW campus magnitude | Comment
Domestic / staff (about 300 people at the 45 L per head per day office norm) | ≈13.5 m³/day | About 80% returns as sewage; on-site STP reuse
Cleaning, housekeeping | 3–10 m³/day | —
Humidification | 0–20 m³/day, seasonal | Dry months (January–March, relative humidity 25–40%) need humidification; the monsoon needs dehumidification, which yields recoverable condensate
Landscaping | 5–20 m³/day | Should use STP or rainwater
Fire suppression | Hundreds of m³ stored; 1–5 m³/week testing | Storage, not consumption
Diesel generator cooling | Closed radiator loops; negligible | —
RO reject | 20–35% of RO feed | Raises withdrawal and discharge, not consumption
Construction | Tens of thousands of m³ over 18–36 months (estimate) | Meta reports construction water separately; Yotta's Greater Noida site had a 50 KLD STP-water connection for construction (DTE)
R6-T04 Freshwater vs recycled water sources (Bengaluru)
Source: Report 6 (full research report) · 1. How much water? › 1.4 Freshwater vs recycled water
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 6 water balance source options; simulator water sources.
Used to derive: Source choice and cycles of concentration.
Source | Bengaluru status | Cooling-tower issues | Implications
BWSSB potable (Cauvery) | Industrial tariff about ₹99/kL | Low TDS allows high CoC | Diverts drinking water; last resort
Groundwater (borewell or tanker) | All Bengaluru Urban taluks over-exploited | TDS 500–1,500 mg/L; silica 20–60 mg/L limits CoC to about 3–4 | Highest local impact; KGWA permits
Tertiary treated wastewater (TTW) | Growing; K&C Valley already sends treated water to Kolar and Chikkaballapur tanks | Ammonia, phosphate, biofouling; needs UF/RO | Has downstream claimants
Rainwater | About 900 mm/yr; a 10 ha roof yields about 80,000 m³/yr | Ideal make-up | About 13% of a 50 MW evaporative plant's need
Seawater | Not available in Bengaluru | Corrosion | Coastal sites only
R6-T05 Daily and annual water demand by capacity and cooling
Source: Report 6 (full research report) · 1. How much water? › 1.5 Daily and annual demand: worked examples
Note: Assumptions: 80% average load, so 1 MW = 19.2 MWh/day = 7,008 MWh/yr of IT energy. WUE is withdrawal-based (L/kWh = m³/MWh).
Data basis: Calculated (model output)
Used in atlas: Ch 6 and Ch 12 reference values.
Used to derive: Daily and annual water per MW and design.
IT capacity | Evaporative, CoC 5 (WUE 1.80) | Adiabatic (0.40) | Dry / DLC (0.05) | WELL Labs basis (26 ML/MW/yr)
1 MW | 34.6 m³/d · 12.6 ML/yr | 7.7 m³/d · 2.8 ML/yr | 1.0 m³/d · 0.35 ML/yr | 71 m³/d · 26 ML/yr
20 MW | 0.69 MLD · 252 ML/yr | 154 m³/d · 56 ML/yr | 19 m³/d · 7 ML/yr | 1.42 MLD · 520 ML/yr
50 MW | 1.73 MLD · 631 ML/yr | 384 m³/d · 140 ML/yr | 48 m³/d · 17.5 ML/yr | 3.56 MLD · 1,300 ML/yr
100 MW | 3.46 MLD · 1,261 ML/yr | 768 m³/d · 280 ML/yr | 96 m³/d · 35 ML/yr | 7.12 MLD · 2,600 ML/yr
R6-T06 Water balance: 50 MW evaporative facility at different CoC
Source: Report 6 (full research report) · 2. Water balance › 2.3 Worked balance: 50 MW Bengaluru hyperscale facility (evaporative)
Note: Annual balance (ML/yr):
Data basis: Calculated (model output)
Used in atlas: Ch 6 "Cooling-tower water balance" calculator.
Used to derive: Withdrawal, consumption, discharge at each CoC.
Stream | CoC 3 (hard borewell) | CoC 5 (potable or softened) | CoC 8 | CoC 8 on TTW + RO (75% recovery) | ZLD
Evaporation | 504.6 | 504.6 | 504.6 | 504.6 | 504.6
Blowdown | 252.3 | 126.2 | 72.1 | 72.1 | 0
Drift | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Tower make-up | 758.1 | 632 | 577.9 | 577.9 | ≈506
RO reject | — | — | — | 192.6 | 0
Non-cooling | 14.6 | 14.6 | 14.6 | 14.6 | 14.6
Withdrawal | 772.7 (2.12 MLD) | 646.6 (1.77 MLD) | 592.5 (1.62 MLD) | 785.1 (2.15 MLD) | ≈525 (1.44 MLD)
Discharge | 264 | 137.9 | 83.8 | 276.4 | ≈0
Consumption | 508.7 (1.39 MLD) | 508.7 | 508.7 | 508.7 | ≈525
Consumption ÷ withdrawal | 66% | 79% | 86% | 65% | ≈100%
Site WUE, withdrawal | 2.21 | 1.85 | 1.69 | 2.24 | 1.5
Site WUE, consumption | 1.45 | 1.45 | 1.45 | 1.45 | 1.5
R6-T07 Water balance: 100 MW AI facility (DLC + adiabatic)
Source: Report 6 (full research report) · 2. Water balance › 2.4 Worked balance: 100 MW AI facility (DLC + adiabatic dry coolers)
Note: Inputs: 100 MW × 85% = 744,600 MWh/yr of IT energy; PUE 1.15; all heat to dry coolers. Adiabatic sprays run about 1,000 h/yr (an illustrative assumption, mostly March–May afternoons) at about 1.0 L/kWh.
Data basis: Calculated (model output)
Used in atlas: Ch 6 text; Ch 12 Example C reasoning.
Used to derive: DLC water and peak factor (3.5×).
Item | Calculation | Annual
Adiabatic water | 85,000 kW × 1,000 h × 1.0 L/kWh | 85 ML
Non-cooling | 30 m³/d | 11 ML
Coolant top-up | — | ≈1 ML
Total withdrawal | — | ≈97 ML/yr (0.27 MLD)
Site WUE | 97 ML ÷ 744,600 MWh | ≈0.13 L/kWh
Consumption | — | ≈80 ML
One-time fill | 1.5–3 L/kW × 100 MW | 150–300 m³
Peak day (May) | 10 h × 90 MW × 1.0 + 30 m³ | ≈0.93 MLD (peak ÷ average ≈ 3.5)
Off-site (grid) | 744,600 × 1.15 × 1.5 L/kWh | ≈1,284 ML/yr (3.5 MLD), about 13× on-site
R6-T08 Water measurement and accounting standards
Source: Report 6 (full research report) · 2. Water balance › 2.5 Measurement and accounting standards
Note: Meters: M1 intake by source (borewell telemetry, tanker logs); M2 RO permeate and reject; M3 tower make-up; M4 blowdown; M5 humidifier feed; M6 domestic and STP; M7 reuse; M8 final discharge. Add conductivity for continuous CoC and 15-minute logging.
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Reference only (metering and standards).
Used to derive: Disclosure design.
Standard | What it requires | Relevance
ISO 46001:2019 | Water-efficiency management system (baselines, indicators, Plan-Do-Check-Act) | Management wrapper
AWS Standard 2.0 | Site + catchment stewardship, certification | Best fit for "impact"
GRI 303 | Withdrawal, discharge, consumption by source and stressed area | Used company-wide, not per site
CDP Water Security | Facility-level data in stressed basins | Few Indian respondents
SEBI BRSR Core | Assured withdrawal by source, consumption, intensity, discharge | Listed companies only (for example Bharti Airtel, parent of Nxtra)
EU Delegated Regulation 2024/1364 | Sites ≥500 kW report total water input (W_IN) and potable input (W_IN-POT); WUE = W_IN ÷ E_IT; annually by 15 May | Template. The 2024 EU average WUE was 0.58 against the Climate Neutral Data Centre Pact target of 0.4.
ISO/IEC 30134-9:2022 | WUE KPI with withdrawal-type and consumption-type categories | Like-for-like if category declared
The Green Grid WUE | Site and source WUE | Original definition
R6-T09 Water per MW of IT capacity
Source: Report 6 (full research report) · 3. Water intensity metrics › 3.2 L/MW (per MW of IT capacity)
Note: L/MW/yr = WUE × 8,760 × load factor × 1,000.
Data basis: Calculated (model output)
Used in atlas: Reference only (per-MW benchmark).
Used to derive: Water per MW for allocations.
Case | WUE | Annual per MW | Daily per MW
Evaporative, CoC 5 | 1.8 | 12.6 ML | 34.6 m³
Evaporative, CoC 3 | 2.21 | 15.5 ML | 42.4 m³
WELL Labs heuristic | ≈3.0 (100% load) | 26 ML | 71 m³
Adiabatic | 0.4 | 2.8 ML | 7.7 m³
Dry | 0.05 | 0.35 ML | 1.0 m³
R6-T10 Water per GPU-hour
Source: Report 6 (full research report) · 3. Water intensity metrics › 3.4 L/GPU-hour
Note: GB200 NVL72: about 120 kW per rack (72 GPUs).
Data basis: Calculated (model output)
Used in atlas: Ch 6 text (water per GPU-hour).
Used to derive: Water per GPU-hour.
Accelerator | On-site, evaporative (1.80) | On-site, DLC (0.13) | Off-site (PUE × 1.5) | Total (evaporative / DLC)
H100 per GPU-hour | 1.8 L | 0.13 L | 1.95 / 1.73 L | 3.75 / 1.86 L
B200 per GPU-hour | 2.5 L | 0.18 L | 2.7 / 2.4 L | 5.2 / 2.6 L
GB200 NVL72 per rack-hour | n/a (requires DLC) | 15.6 L | 207 L | ≈223 L (≈3.1 L per GPU-hour)
R6-T11 Water per inference and training
Source: Report 6 (full research report) · 3. Water intensity metrics › 3.5 L/inference and training
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 6 "Water per AI prompt" chart.
Used to derive: Per-prompt water by boundary.
Source | Figure | Boundary
Google (August 2025) | 0.26 mL per median Gemini Apps text prompt (0.24 Wh); narrow approach 0.12–0.15 mL | On-site consumption; fleet-average WUE; excludes electricity water; prompt length unspecified
Sam Altman (June 2025) | ≈0.32 mL; 0.34 Wh | Method undisclosed
Li, Yang, Islam & Ren (UC Riverside), *Making AI Less Thirsty* | 500 mL per 10–50 GPT-3 responses. The paper's India column: 19.7 mL per request, all off-site (on-site WUE 0, EWIF 3.445). | On-site + off-site
Mistral AI LCA (Carbone 4, ADEME) | 45 mL per 400-token response; 1.14 gCO₂e | Full life cycle; training + inference = 91% of water
GPT-3 training | 5.4 ML total incl. 0.7 ML on-site (US); India case 6.34 ML | Li et al.
Mistral Large 2 | 281,000 m³ (training + 18 months of use) | LCA
R6-T12 Which water metric for which audience
Source: Report 6 (full research report) · 3. Water intensity metrics › 3.6 Which metric for which audience, pitfalls and normalisation
Data basis: Illustrative / framework / author judgement
Used in atlas: Reference only.
Used to derive: Which metric for regulator, customer, citizen.
Audience | Best metrics
Operator | Monthly site WUE, CoC, make-up per tower cell
Regulator / utility (BWSSB, KGWA, KSPCB) | Withdrawal by source (MLD, peak day), consumption, discharge quality
Customer | Source WUE, L/GPU-hour, L/inference with declared boundary
Citizen | Share of ward or taluk supply, people-equivalents, scarcity-weighted footprint
Investor | Consumption in stressed areas; replenishment vs consumption
R6-T13 Bengaluru scenarios compared (S1–S4)
Source: Report 6 (full research report) · 3. Water intensity metrics › 3.7 Single comparison table: Bengaluru scenarios
Data basis: Calculated (model output)
Used in atlas: Ch 6 Bengaluru scenario table.
Used to derive: Site vs source WUE for S1–S4.
Metric | S1: 20 MW colocation, evaporative (PUE 1.40, 70%) | S2: 50 MW hyperscale, evaporative, CoC 5 (PUE 1.30, 80%) | S3: 50 MW dry (PUE 1.45, 80%) | S4: 100 MW AI DLC + adiabatic (PUE 1.15, 85%)
IT energy (GWh/yr) | 122.6 | 350.4 | 350.4 | 744.6
Site withdrawal (ML/yr; MLD) | 221; 0.60 | 647; 1.77 | 17.5; 0.05 | 97; 0.27
Peak day (MLD) | 0.81 | 2.4 | 0.05 | 0.93
Site WUE / L per MWh | 1.80 / 1,800 | 1.85 / 1,850 | 0.05 / 50 | 0.13 / 130
Off-site (PUE × 1.5) | 2.1 | 1.95 | 2.18 | 1.73
Total / source WUE | 3.9 | 3.8 | 2.23 | 1.86
ML/MW/yr (site) | 11 | 12.9 | 0.35 | 0.97
L per server-hour (0.5 kW), site / total | 0.90 / 1.95 | 0.93 / 1.90 | 0.025 / 1.11 | 0.065 / 0.93
L per H100-hour, site / total | 1.8 / 3.9 | 1.85 / 3.8 | 0.05 / 2.2 | 0.13 / 1.9
mL per 0.3 Wh prompt, site / total | 0.39 / 0.84 | 0.43 / 0.88 | 0.01 / 0.46 | 0.03 / 0.48
R6-T14 Bengaluru sector water-use estimates
Source: Report 6 (full research report) · 4. Local context › 4.1 Data centre use against Bengaluru's water availability
Note: Sector use: estimates disagree fivefold:
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 4 "How much do Bengaluru's data centres use today?" chart.
Used to derive: Range of sector water estimates.
Estimate | Value | Basis
Karnataka IT department (2026) | ≈4 MLD across 32 facilities statewide | Informal "industry-wide approximation"
WELL Labs (Shashank Palur) | ≈20 MLD | 26 ML/MW/yr × capacity (about 292 MW across 18 centres)
DTE permissions (2013–2025) | ≈812.9 ML/yr (≈2.2 MLD) | Allocations, not use
BWSSB billing | 129,000 L/month for five centres | Shared meters make it meaningless
This report | 292 MW × 70% × 24 h × 1.8 ≈ 8.8 MLD if all evaporative; about 4–5 MLD if half air-cooled | Cooling mix explains the gap
R6-T15 Equivalence metrics (S2, 50 MW evaporative)
Source: Report 6 (full research report) · 4. Local context › 4.3 Equivalence metrics (S2, 50 MW evaporative)
Data basis: Calculated (model output)
Used in atlas: Ch 6 "Water you can picture" (people, tankers, pools).
Used to derive: Everyday equivalents of site water.
Equivalence | Result
People at 135 LPCD (1.77 MLD) | ≈13,100 people
Households (675 L/d) | ≈2,600 households
Paddy (≈12,500 m³/ha per season, typical value) vs 508,700 m³ consumed | ≈41 ha
Ragi (≈4,000 m³/ha) | ≈127 ha
WELL Labs framing, 20 MLD sector-wide | "drinking water for around 1.3 lakh people"
Karnataka's 1 GW target, all evaporative at S2 intensity | ≈12.9 GL/yr ≈ 35 MLD (about 1.8% of BWSSB delivered supply); about 71 MLD at WELL Labs intensity
1 GW, DLC or dry | ≈1–3 MLD on site
1 GW off-site (80% load, PUE 1.3, 1.5 L/kWh) | ≈37 MLD, regardless of cooling
R6-T16 Water-stress frameworks
Source: Report 6 (full research report) · 5. Water stress › 5.1 Frameworks
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Reference only (water-stress frameworks).
Used to derive: Choice of scarcity method.
Framework | Definition | Scale | Bengaluru / India
WRI Aqueduct 4.0 baseline water stress | Withdrawal ÷ available renewable supply (sub-basin) | Low <10%, low–medium 10–20%, medium–high 20–40%, high 40–80%, extremely high >80% | WRI lists India among the 25 "extremely high" countries (2023); a 2026 preprint scores it 3.05 ("high"). Conflict flagged. WRI India finds more than half of India's data centres in high or extremely-high stress areas. S&P Global Sustainable1 (September 2025) projects that "60% to 80%" of India's operating data centres will face high water stress this decade, with an average data centre water stress index of 62. Sub-basin scores for Bengaluru, Cauvery, Krishna (Raichur) and Pennar were not verifiable from text sources.
AWARE (WULCA) | CF = world-average available water remaining per area ÷ regional value | 0.1–100 m³ world-eq/m³; consumption-weighted world averages 43 (unspecified), 20 (non-agricultural), 46 (agricultural) | India sub-national CFs exist in AWARE 1.2; AWARE 2.0 (2025) generally lowers CFs. India and basin values not verified here. Scenario values are used below.
WWF Water Risk Filter | Composite basin physical, regulatory and reputational risk | 1–5 | Portfolio screening
CGWB stage of extraction | Extraction ÷ extractable recharge | Safe <70, semi-critical 70–90, critical 90–100, over-exploited >100% | Most relevant locally: Bangalore East 305%, Devanahalli 169%
Falkenmark | Renewable m³/person/year | <1,700 stress; <1,000 scarcity; <500 absolute | India near or below 1,700 nationally (approximate). Bengaluru's delivered water is about 80 m³/person/year, almost all imported Cauvery water.
R6-T17 Proposed materiality thresholds
Source: Report 6 (full research report) · 5. Water stress › 5.2 Methods
Note: 2. Materiality thresholds (proposed by this report):
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 6 thresholds logic (reference).
Used to derive: Materiality tests for permits.
Ratio | Disclose | Significant | Material
Consumption ÷ catchment renewable availability | >0.1% | >1% | >5%
Withdrawal ÷ ward or zone supply | >1% | >5% | >10%
Groundwater withdrawal ÷ taluk recharge | any (over-exploited) | >0.5% | >1% or any evaporative use in over-exploited taluks
Peak-month withdrawal ÷ summer deficit | >0.5% | >2% | >5%
R6-T18 Scarcity-weighted footprint by scenario (50 MW)
Source: Report 6 (full research report) · 5. Water stress › 5.3 Applying the methods to Bengaluru scenarios (50 MW, annual)
Note: Off-site consumption is facility energy × 1.5 L/kWh: 683 ML/yr for evaporative and 762 ML/yr for dry. A renewable PPA has an EWIF of about 0.1.
Data basis: Calculated (model output)
Used in atlas: Ch 6 "Scarcity-weighted water footprint" chart.
Used to derive: Footprint ranking of design and source options.
Scenario | On-site consumption (ML/yr) | CF | On-site WSF (Mm³-eq) | Off-site (ML/yr) | Off-site WSF | Total WSF | Materiality
A. Evaporative, Bangalore East groundwater | 508.7 | 100 | 50.9 | 683 | 34.2 | 85 | 3.9% of taluk recharge: material
B. Evaporative, BWSSB potable | 508.7 | 60 | 30.5 | 683 | 34.2 | 64.7 | 0.09% of city supply, but drinking water: significant
C. Evaporative, TTW + RO | 508.7 | 30 | 15.3 | 683 | 34.2 | 49.4 | Competes with K&C Valley: disclose
D. Dry, municipal top-up | 17.5 | 60 | 1.1 | 762 | 38.1 | 39.2 | Immaterial on site
E. Dry + renewable PPA | 17.5 | 60 | 1.1 | 51 | 2.5 | 3.6 | Immaterial
F. 100 MW AI DLC on TTW | ≈80 | 30 | 2.4 | 1284 | 64.2 | 66.6 (13.6 with PPA) | Off-site dominated
R6-T19 Water impact scorecard
Source: Report 6 (full research report) · 5. Water stress › 5.4 Water impact scorecard
Note: Scores run from 1 (low) to 5 (high impact); weights in brackets.
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 6 "Impact scorecard" table.
Used to derive: Refuse / redesign / acceptable decision per scenario.
Dimension (weight) | A. Evaporative, groundwater | B. Evaporative, potable | C. Evaporative, TTW + RO | D. Dry | F. AI DLC on TTW | E. Dry + PPA
Volume (20%): consumption per MW | 5 | 5 | 5 | 1 | 2 | 1
Source (25%): over-exploited groundwater 5 … none 1 | 5 | 4 | 3 | 2 | 3 | 2
Timing (15%): peak and summer coincidence | 4 | 4 | 4 | 1 | 4 | 1
Location / stress (25%) | 5 | 4 | 4 | 4 | 4 | 4
Off-site (15%) | 3 | 3 | 3 | 4 | 3 | 1
Weighted score | 4.6 | 4 | 3.8 | 2.6 | 3.3 | 1.9
Decision (≥4 refuse/redesign; 3–4 conditional; <3 acceptable) | Refuse | Redesign | Conditional | Acceptable | Conditional (peak cap, PPA) | Preferred
R6-T20 Hyperscaler water reporting: practices and gaps
Source: Report 6 (full research report) · Hyperscaler and Indian operator water reporting: practices and gaps
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 6 disclosure text; Ch 12 fleet dots.
Used to derive: Benchmark WUE values of operators.
Company | Latest disclosures | Gaps
Google | 2024 consumption 8.1 billion gallons (+28%); replenished 4.5 billion gallons = 64% (18% in 2023); original target 120% by 2030. Secondary summaries of the 2026 report show 2025 consumption of about 10.9 billion gallons (+34%) and more than 7 billion gallons replenished. The June 2026 pledge is to replenish more than it consumes at its sites by 2030 (165 projects, 97 watersheds). | Consumption growing faster than replenishment; replenishment not necessarily in the same catchment; per-prompt figure excludes electricity water
Microsoft | WUE 0.30 (FY2024, withdrawal), down from 0.49 (2021); zero-water-evaporation designs since August 2024 (pilots at Phoenix and Mt Pleasant from 2026, coming online from late 2027), which Microsoft's VP of Datacenter Infrastructure Engineering Steve Solomon says will save more than 125 million litres of water per datacenter per year | "Nominal" energy increase; claims not independently reviewed; legacy fleet still evaporative
AWS | WUE 0.15 (2024) and 0.12 (2025); 53% → 75% toward water positive by 2030; claims water positive in India (returned 120% in 2025) | No Indian site volumes or sources; relies on replenishment accounting
Meta | WUE 0.19 (2024); consumption 3,123 ML; restores 200% (high stress) and 100% (medium stress); 1.6 billion gallons restored in 2024; construction water reported separately | US-centric
R6-T21 Minimum water disclosure framework
Source: Report 6 (full research report) · Recommendations › A. Minimum measurement and disclosure framework (all sites ≥500 kW IT)
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 6 "Seven metrics every site should publish".
Used to derive: Minimum disclosure standard.
# | Metric | Granularity | Basis
1 | Withdrawal by source (potable, groundwater, tanker, TTW, rainwater) | m³, monthly, per site | GRI 303-3; EU 2024/1364
2 | Consumption (withdrawal − discharge, cross-checked by CoC) | m³, monthly | GRI 303-5; ISO 14046
3 | Discharge volume and quality | m³, mg/L | GRI 303-4; CPCB / KSPCB
4 | Site WUE, withdrawal and consumption (ISO/IEC 30134-9 category declared) | L/kWh, monthly and annual | The Green Grid
5 | Source WUE (location-based and market-based) | L/kWh | The Green Grid
6 | Scarcity-weighted footprint (on-site + off-site) | m³ world-eq (AWARE version declared) | ISO 14046
7 | Seasonal profile | Peak-day MLD, peak-month ÷ average, storage hours | —
+ | Context ratios | Share of taluk groundwater and ward supply | CGWB / BWSSB
R6-T22 Suggested water thresholds
Source: Report 6 (full research report) · Recommendations › C. Suggested thresholds
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 6 "Suggested thresholds" table.
Used to derive: Green/amber/red ratings.
Indicator | Green | Amber | Red
Site consumption WUE (L/kWh) | ≤0.2 | 0.2–1.0 | >1.0
Groundwater for cooling, over-exploited taluks | 0% | — | >0%
Withdrawal ÷ taluk recharge | <0.5% | 0.5–1% | >1%
Peak ÷ average without curtailment plan | <1.5 | 1.5–3 | >3
Source WUE (L/kWh) | <1.0 | 1.0–2.5 | >2.5
Scorecard | <3 | 3–4 | ≥4

## R7
Report 7 · Unit economics
24 tables. Source line under each title; "Note" gives the context sentence from the report.
R7-T01 Construction cost index by market (Turner & Townsend)
Source: Report 7 (full research report) · 1. CAPEX (₹) › 1.1 Global and Indian benchmarks
Note: Turner & Townsend Data Centre Construction Cost Index 2025–26 (52 markets, traditional air-cooled cloud data centre, US$ per watt; construction only):
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 7 "Build cost around the world" chart; Key numbers.
Used to derive: Mumbai cost advantage; forecast base cost.
Market | US$/W | ₹ crore/MW (at ₹90/$) | Comment
Tokyo | 15.2 | 137 | Most expensive
Singapore | 14.5 | 131 | 2nd
Zurich | 14.2 | 128 | 3rd
Silicon Valley | 13.3 | 120 | Largest US premium
New Jersey | 12.9 | 116
Oslo | 12.4 | 112 | 7th
London | 12 | 108
Frankfurt | 11.6 | 104
Atlanta | 9.9 | 89
Phoenix / Columbus | 9.8 | 88
Charlotte | 9.5 | 86
Mumbai | 6.64 | 60 | 51st of 52
R7-T02 Land prices in Indian data-centre hubs
Source: Report 7 (full research report) · 1. CAPEX (₹) › 1.2 Land and buildings
Note: Land prices per acre in Indian data centre hubs. Transaction-based figures are labelled. The rest are estimates or come from low-quality sources.
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 7 "Land and power" table; simulator land prices.
Used to derive: Land share of capex by hub.
Hub | ₹ crore/acre | Evidence
Navi Mumbai (TTC MIDC, Airoli, Mahape, Ghansoli) | 15–40 greenfield; up to ~80 for in-fill with structures | STT GDC paid ₹282 crore for 14,093 m² (~3.5 acres) with an existing 6,828 m² building (May 2026), ≈₹81 crore/acre. Brookfield paid ₹600 crore for 30 acres in Ghansoli (2021), ≈₹20 crore/acre.
Thane / Palava (MMR periphery) | 12–35 | AWS: ~40–45 acres at Palava for ₹500–600 crore (≈₹12–14 crore/acre). Amazon: 54 acres in Thane for ₹1,870 crore (≈₹35 crore/acre).
Chennai (Ambattur, Oragadam, Siruseri) | 8–15 Ambattur; 3–8 Oragadam (estimate) | A secondary blog source gives ₹8–15 crore/acre; treat as indicative.
Hyderabad | 2–6 | Microsoft bought 48 acres for ₹267 crore (2024), ≈₹5.6 crore/acre.
Noida / Greater Noida | 3–10 (estimate, not verified) | Authority allotment rates vary; check YEIDA and GNIDA schedules.
Bengaluru Whitefield | 10–25 (estimate, not verified)
Bengaluru Devanahalli / Hoskote | 4–10 (estimate, not verified)
Pune (Hinjewadi, Chakan, Talegaon) | 5–15 (estimate, not verified)
R7-T03 Servers, storage and GPU prices
Source: Report 7 (full research report) · 1. CAPEX (₹) › 1.3 Servers, storage and GPUs (IT capex)
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 7 GPU calculator (HGX prices); simulator GPU capex.
Used to derive: IT capex per MW and per GPU.
Item | Price (USD) | India landed (₹, at ₹90/$) | Notes
CPU server, dual-socket 1U/2U cloud node | US$9–22k (estimate) | ₹8–20 lakh | Not verified; varies hugely with configuration
Storage | ~₹45–90 lakh per PB raw (estimate) |  | Not verified
H100 SXM card | US$25–40k | ₹22–36 lakh | Multiple 2026 price guides
H100 HGX 8-GPU server | US$250–320k | ₹2.25–2.9 crore
H200 HGX 8-GPU server | ~US$300–330k (estimate) | ~₹2.7–3.0 crore | H200 cards quoted at US$30–35k
B200 HGX 8-GPU server | US$400–500k (DGX B200 lists ~US$515k) | ₹3.6–4.5 crore
GB200 NVL72 rack | US$3.0M (HSBC); US$3.1M bare / US$3.9M all-in (SemiAnalysis) | ₹27–35 crore | 72 GPUs, ~120–135 kW
GB300 NVL72 rack | US$3.7–4.0M (Loop Capital) vs US$6.0–6.5M (Tom's Hardware supply chain, March 2026); ~US$5.0M purchase / US$5.7M deployed (Data Gravity) | ₹33–58 crore | Estimates disagree; Supermicro datasheet lists 132–140 kW
R7-T04 Soft costs, interest during construction and contingency
Source: Report 7 (full research report) · 1. CAPEX (₹) › 1.8 Soft costs, interest during construction and contingency
Data basis: Proxy / estimate
Used in atlas: Capex stacks (soft costs, contingency, IDC).
Used to derive: Soft-cost share of capex.
Item | Typical share | Our base
Design, permits, project management (PMC), commissioning | 5–8% of hard cost | 5–6%
Contingency | 5–10% | 5–6.5%
Interest during construction (IDC) | 18–24-month build; ~70% debt at ~9.5%; average 50% drawn | ≈5–6% of facility cost
R7-T05 Capex breakdown: 20 MW Tier III colocation
Source: Report 7 (full research report) · 1. CAPEX (₹) › 1.9 Breakdown tables for the three cases
Note: (a) 20 MW Tier III colocation (Navi Mumbai/Chennai-type; air-cooled chilled water; 2N electrical, N+1 DG; multi-storey on 5 acres at ₹20 crore/acre)
Data basis: Calculated (model output)
Used in atlas: Ch 7 "Line by line" table (Case A) and capex chart; simulator colo capex ₹56.1 cr/MW.
Used to derive: Capex per MW for a colo.
Item | ₹ crore/MW | ₹ crore (20 MW) | Share of facility capex
Land (0.25 acre/MW) | 5 | 100 | —
Shell and core, civil/structural | 8.5 | 170 | 15.2%
Electrical (substation share, transformers, switchgear, 2N UPS, PDUs, busway) | 22 | 440 | 39.2%
Cooling (chillers, towers/adiabatic, CRAH, piping) | 10 | 200 | 17.8%
Backup (DG N+1 ~42 MVA, fuel) | 4.2 | 84 | 7.5%
Fire, BMS/DCIM, security, low-voltage | 2 | 40 | 3.6%
Networking (meet-me rooms, fibre entry, cabling) | 1 | 20 | 1.8%
Hard cost subtotal | 47.7 | 954 | 85.0%
Design, permits, PMC (~6%) | 3 | 60 | 5.3%
Contingency (~5%) | 2.5 | 50 | 4.5%
Interest during construction | 2.9 | 58 | 5.2%
Facility total (excl. land) | 56.1 | 1122 | 100%
Total incl. land | 61.1 | 1,222 (≈US$136M) | Land = 8%
R7-T06 Capex breakdown: 50 MW hyperscale build-to-suit
Source: Report 7 (full research report) · 1. CAPEX (₹) › 1.9 Breakdown tables for the three cases
Note: (b) 50 MW hyperscale build-to-suit (Hyderabad/Chennai-type; developer delivers shell and M&E, tenant supplies IT; 20 acres at ₹8 crore/acre)
Data basis: Calculated (model output)
Used in atlas: Ch 7 "Line by line" (Case B); simulator hyperscale ₹39.2 cr/MW.
Used to derive: Capex per MW for hyperscale.
Item | ₹ crore/MW | ₹ crore (50 MW) | Share of facility capex
Land (0.4 acre/MW) | 3.2 | 160 | —
Shell and core | 5.5 | 275 | 14.0%
Electrical (incl. 220 kV substation) | 15.5 | 775 | 39.5%
Cooling | 7.5 | 375 | 19.1%
Backup (DG) | 3.3 | 165 | 8.4%
Fire, BMS, security | 1.4 | 70 | 3.6%
Networking / meet-me rooms | 0.3 | 15 | 0.8%
Hard cost subtotal | 33.5 | 1675 | 85.5%
Soft costs (5%) | 1.7 | 85 | 4.3%
Contingency (5%) | 1.7 | 85 | 4.3%
Interest during construction | 2.3 | 115 | 5.9%
Facility total | 39.2 | 1960 | 100%
Total incl. land | 42.4 | 2,120 (≈US$236M) | Land = 7.5%
R7-T07 Capex breakdown: 100 MW AI campus incl. GPUs
Source: Report 7 (full research report) · 1. CAPEX (₹) › 1.9 Breakdown tables for the three cases
Note: (c) 100 MW AI campus including GPUs (liquid-cooled; GB300 NVL72-class at ~135 kW/rack; Hyderabad/AP/Devanahalli-type land at ₹5 crore/acre)
Data basis: Calculated (model output)
Used in atlas: Ch 7 "Line by line" (Case C); simulator AI ₹72.5 + ₹266 cr/MW.
Used to derive: Capex per MW for an AI campus incl. GPUs.
Item | ₹ crore/MW | ₹ crore (100 MW) | Share
Land (0.3 acre/MW, 30 acres) | 1.5 | 150 | 0.4% of total
Shell and core | 7 | 700 | 9.7% of facility
Electrical (400/220 kV substation, high-ampacity busway, UPS) | 28 | 2800 | 38.6%
Cooling (CDUs, DLC loops, dry coolers, trim chillers) | 17 | 1700 | 23.4%
Backup (DG N+1 + BESS) | 6 | 600 | 8.3%
Fire, BMS | 2 | 200 | 2.8%
Network infrastructure (meet-me rooms, fibre) | 1 | 100 | 1.4%
Soft costs / contingency / IDC | 3.5 / 4.0 / 4.0 | 350 / 400 / 400 | 15.8%
Facility total (excl. land) | 72.5 | 7250 | 21.3% of total
GPU racks: ~590 × GB300 NVL72 at ~US$4.2M | 223 | 22300
Back-end fabric (~12% of cluster) | 32 | 3240
Storage, front-end, CPU, management | 11 | 1080
IT total (42,480 GPUs) | 266 | 26620 | 78.2% of total
Campus total | ~340 | ~34,020 (≈US$3.8 billion) | IT/facility = 3.7×
R7-T08 State HT/EHT tariffs for data centres (FY2025–26)
Source: Report 7 (full research report) · 2. OPEX (₹) › 2.1 Electricity
Note: State HT/EHT tariffs relevant to data centres (FY2025–26 orders; energy charge plus demand charge; excludes electricity duty, ToD and fuel adjustments):
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Simulator tariffs (KA, MH, TN, TG); Ch 7 land and power table.
Used to derive: Power bill and LCOD.
State | Category / voltage | Energy ₹/kWh | Demand ₹/kVA/month | DC-specific relief
Karnataka | HT industrial (prior report) | ~6.70 | ~365 | See prior report
Maharashtra (MSEDCL) | HT-I(A) Industry | 7.27 | 560 | MERC: 10% wheeling-charge discount for data centres sourcing green power via open access or green tariff. State policy: ₹1/unit tariff subsidy for 5 years for certain new data centre units. MERC's March 2025 multi-year order was later subject to review; verify the current schedule.
Tamil Nadu (TNERC) | HT-I | 7.5 | 608 (up from 589) | 100% electricity tax subsidy for 5 years for data centres. Green tariff = 110% of category tariff. ToD: +25% peak, −5% night.
Telangana (TGERC) | HT-I(A) at 132 kV / 33 kV / 11 kV | 6.65 / 7.15 / 7.65 | 500 | Data centres pay 60% (wind) / 70% (solar) of conventional cross-subsidy surcharge.
Uttar Pradesh, Andhra Pradesh, Gujarat | HT industrial | Not verified in this research (typically ₹7–8) | — | Check UPERC, APERC and GERC orders. Andhra Pradesh hosts Google's planned US$6 billion, 1 GW project.
R7-T09 Annual electricity cost by tariff and case
Source: Report 7 (full research report) · 2. OPEX (₹) › 2.1 Electricity
Note: Case C: 100 MW × PUE 1.25 = 125 MW, 1,095 GWh, 138 MVA
Data basis: Calculated (model output)
Used in atlas: Reference for simulator power bill.
Used to derive: Annual electricity cost by state.
Tariff | Case A (20 MW colo) | Case B (50 MW hyperscale) | Case C (100 MW AI) | Effective ₹/kWh
Karnataka (6.70 + 365) | 190.5 | 444.5 | 794.1 | ~7.25
Maharashtra (7.27 + 560) | 213.3 | 497.5 | 888.8 | ~8.1 (before ₹1 subsidy)
Tamil Nadu (7.50 + 608) | 221.2 | 516.1 | 922 | ~8.4 (≈8.9 with ToD for a flat load)
Telangana 132 kV (6.65 + 500) | 194.6 | 454 | 811 | ~7.4
Green RTC via group captive (~6.5 + grid demand ~500) | ~190.6 | ~444.8 | ~794.6 | ~7.25
R7-T10 Water bill by case
Source: Report 7 (full research report) · 2. OPEX (₹) › 2.2 Water
Note: The prior water report gave about 0.6–1.8 MLD for evaporative cases. Tariff anchors are BWSSB industrial at about ₹99/kL and treated water at ₹10–20/kL. MIDC, CMWSSB and HMWSSB tariffs were not re-verified here.
Data basis: Calculated (model output)
Used in atlas: Simulator water cost line.
Used to derive: Water cost share of opex (<2%).
Case | Assumed draw | kL/yr | Bill at ₹99/kL | Bill at ₹15/kL (treated)
A: 20 MW colo (evaporative) | 0.3 MLD | 109500 | ₹1.08 crore | ₹0.16 crore
B: 50 MW hyperscale | 0.6 MLD | 219000 | ₹2.17 crore | ₹0.33 crore
C: 100 MW AI (hybrid; DLC + dry coolers can be far lower) | 1.0 MLD (up to 1.8) | 365,000 (657,000) | ₹3.6 (6.5) crore | ₹0.55 (0.99) crore
R7-T11 Indian salary markers
Source: Report 7 (full research report) · 2. OPEX (₹) › 2.5 Personnel
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Reference only (personnel cost basis).
Used to derive: Staff cost per FTE.
Role | Pay | Source
Data centre critical-facilities engineer | ~₹20.8 lakh average; ₹14.8 lakh at 1–3 years | SalaryExpert, Aug 2026; modelled, likely high
NOC engineer | Median ₹4.18 lakh (₹3.1–6.0 lakh interquartile) | Glassdoor India, Jun 2026
NOC engineer | Median ₹4.05 lakh | PayScale, Apr 2026
Data centre manager | Median ₹8.62 lakh (75th percentile ₹20 lakh) | PayScale; large-campus heads earn far more (estimate ₹30–60 lakh)
Security guard, Mumbai/Thane | Statutory cost ₹32,315/month per head for 8-hour duty (≈₹3.9 lakh/yr) | Maharashtra Security Guards Board wage order, Jan–Jun 2026
R7-T12 Opex: Case A, 20 MW colocation
Source: Report 7 (full research report) · 2. OPEX (₹) › 2.8 Opex tables per case (stabilised year)
Note: Case A: 20 MW colo. 90% billed (18 MW); average IT draw 70% of billed (12.6 MW); PUE 1.5; blended energy ₹6.6/kWh (grid plus partial RE).
Data basis: Calculated (model output)
Used in atlas: Ch 7 "Where colo opex goes" chart; LCOD calculator.
Used to derive: Opex per MW, power share.
Line | ₹ crore/yr
Electricity (165.6 GWh × ₹6.6 = 109.3, plus demand charges 19.8) | 129
Water | 0.6
Water treatment and chemicals | 0.4
AMC (2% of ₹764 crore M&E) | 15.3
DG fuel and testing | 1.5
Personnel (60 FTE) | 7.5
Insurance | 2.2
Property tax and levies | 1.5
Network | 1
SG&A | 15
Total opex | 174
₹/kW/month (on 20 MW built) | ₹7,250 (₹1,875 excluding power)
R7-T13 Opex: Case B, 50 MW hyperscale
Source: Report 7 (full research report) · 2. OPEX (₹) › 2.8 Opex tables per case (stabilised year)
Note: Case B: 50 MW hyperscale. 95% billed; IT draw 75% (35.6 MW); PUE 1.4; ₹6.2/kWh; power passed through to the tenant.
Data basis: Calculated (model output)
Used in atlas: Reference (hyperscale opex in LCOD preset B).
Used to derive: Opex per MW for hyperscale.
Line | ₹ crore/yr
Electricity (437 GWh × ₹6.2 = 271, plus demand 33), passed through | 304
Water | 1.2
AMC (1.75% of ₹1,385 crore) | 24.2
DG fuel and testing | 2.5
Personnel (70 FTE) | 8.5
Insurance / property tax / network | 3.5 / 2.5 / 0.5
SG&A | 10
PUE-overrun and SLA reserve | 5
Chemicals | 0.6
Total opex (non-power) | 58.5
Total including pass-through power | 362.5
₹/kW/month | ₹6,040 total; ₹975 non-power
R7-T14 Opex: Case C, 100 MW AI campus
Source: Report 7 (full research report) · 2. OPEX (₹) › 2.8 Opex tables per case (stabilised year)
Note: Case C: 100 MW AI campus. IT draw 80%; PUE 1.25; RE-RTC-led supply at ₹6.0/kWh.
Data basis: Calculated (model output)
Used in atlas: Reference (AI preset C in LCOD).
Used to derive: Opex per MW for AI campus.
Line | ₹ crore/yr
Electricity (876 GWh × ₹6.0 = 526, plus demand 66) | 592
Water | 2
Facility AMC (2% of ₹5,300 crore M&E) | 106
GPU/IT support and spares (1% of IT capex) | 266
Personnel (150 FTE) | 25
Insurance | 68
Network, backbone, transit | 20
Property tax | 5
SG&A | 100
DG | 3
Total opex | 1187
₹/kW/month | ₹9,890 (facility-only ≈ ₹7,675)
R7-T15 Colocation pricing in India
Source: Report 7 (full research report) · 3. Unit economics › 3.1 ₹ per MW: capex, revenue, EBITDA, payback, IRR, valuation
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Simulator break-even rent comparison; Ch 7 text; Key numbers.
Used to derive: Market rent vs break-even.
Segment | Price | Source
Mumbai, 250 kW–1 MW | ₹7,000–10,000/kW/month | Cushman & Wakefield H1 2025 (standard 5–7 kVA racks)
Mumbai, 1–5 MW | ₹6,500–8,000 | Cushman & Wakefield H1 2025
Mumbai, 5 MW+ | ₹6,000–7,500 | Cushman & Wakefield H1 2025
Chennai, 1–5 MW | ₹7,000–8,000 | Cushman & Wakefield H1 2025
Sub-250 kW, secondary hubs | ₹7,000–9,500 | Cushman & Wakefield H1 2025
India average rent | US$80–100/kW/month (₹7,200–9,000) | Houlihan Lokey
North America wholesale (250–500 kW), for comparison | US$196.25/kW/month (+6.6% year-on-year), about 2× India | CBRE, H2 2025
R7-T16 Per-MW economics by case
Source: Report 7 (full research report) · 3. Unit economics › 3.1 ₹ per MW: capex, revenue, EBITDA, payback, IRR, valuation
Note: Per-MW economics by case (stabilised).
Data basis: Calculated (model output)
Used in atlas: Ch 7 "Returns by business model" table.
Used to derive: EBITDA, payback, IRR per model.
Metric | A: 20 MW colo | B: 50 MW hyperscale build-to-suit | C: 100 MW AI neocloud
Capex/MW, facility only | ₹56.1 crore | ₹39.2 crore | ₹72.5 crore
Capex/MW incl. land and IT | ₹61.1 crore | ₹42.4 crore | ~₹340 crore
Pricing assumption | ₹7,000/kW/mo rent + power at cost +10% | ₹6,250/kW/mo + power at cost | ₹400/GPU-hr at 80% utilisation (assumption)
Revenue (₹ crore/yr) | 301 (rent 151 + power 142 + other 8) | 660 (rent 356 + power 304) | 11908
Opex (₹ crore/yr) | 174 | 362.5 | 1187
EBITDA (₹ crore/yr) | 127 (42% margin) | 298 (45% of gross; 84% of rent) | 10,721 (90%)
EBITDA per MW per year | ₹6.35 crore | ₹5.96 crore | ₹107 crore
Yield on cost (EBITDA ÷ capex) | 10.4% | 14.0% | 31.5% (but GPUs last ~5 years)
Simple payback | ~9.6 years | ~7.1 years | ~3.2 years
Unlevered pre-tax IRR (method below) | ~9.5% | ~14.7% | ~21.5% at 80% / ~10.5% at 60% / negative at 40%
R7-T17 Valuations (EV/MW and EV/EBITDA)
Source: Report 7 (full research report) · 3. Unit economics › 3.1 ₹ per MW: capex, revenue, EBITDA, payback, IRR, valuation
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 7 text (Nxtra valuation).
Used to derive: Value per MW vs replacement cost.
Data point | Implied value
Nxtra, March 2026: US$1 billion raise (Alpha Wave US$435M, Carlyle US$240M, Anchorage US$35M, Airtel about US$290M) at US$3.1 billion post-money; before the deal Airtel held 75.96% and Carlyle the rest; about 300 MW, targeting 1 GW | ~US$7M/MW pre-money (≈₹63 crore/MW); ~US$10M/MW post-money
Earlier Nxtra reference points | Carlyle invested in 2020 at a US$1.2 billion valuation. April 2025 reports of Alpha Wave buying Carlyle's 24% stake implied ₹20,500 crore (US$2.4 billion) for 100%.
Houlihan Lokey cap rates: India 7.5–8.5%; US 4.5–6.5%; Singapore 5.0–6.5% | Stabilised Indian assets at about 12–13× EBITDA (Case A at 8% → about ₹1,590 crore of value vs ₹1,222 crore cost, 1.3×; Case B at 7.5% → about ₹3,970 crore vs ₹2,120 crore, 1.9×)
Sify Infinit Spaces DRHP (Oct 2025): ₹3,700 crore IPO (₹2,500 crore fresh issue); net debt ₹2,324 crore; net debt/EBITDA 3.66× | EV/EBITDA not determinable until pricing
R7-T18 Cost per rack by density
Source: Report 7 (full research report) · 3. Unit economics › 3.2 ₹ per rack
Note: The facility cost per rack scales with density. The wholesale-rent column uses ₹7,500/kW/month.
Data basis: Calculated (model output)
Used in atlas: Reference only (cost per rack).
Used to derive: Capex and rent per rack by density.
Density | Design | Facility ₹ crore/MW | Facility capex per rack | Typical IT per rack | Implied wholesale rent/rack/month
6 kW | Air, Tier III | ~58 | ~₹35 lakh | ₹40–80 lakh of CPU servers (estimate) | ~₹45,000
10 kW | Air + containment | ~55 | ~₹55 lakh | ₹0.8–1.5 crore (estimate) | ~₹75,000
40 kW | Rear-door heat exchangers / DLC hybrid | ~62 | ~₹2.5 crore | ~4 × H100 HGX ≈ US$1.1M ≈ ₹10 crore | ~₹3.0 lakh
130 kW | DLC (NVL72) | ~72.5 | ~₹9.4 crore | GB300 NVL72 ₹33–58 crore + fabric | ~₹9.75 lakh (₹10.4–11.7 lakh at ₹8,000–9,000/kW)
R7-T19 Levelised cost of data-centre capacity (LCOD)
Source: Report 7 (full research report) · 3. Unit economics › 3.3 ₹ per kWh: levelised cost of data centre capacity (LCOD)
Note: LCOD = (Annualised capex + Annual opex) ÷ IT kWh delivered.
Data basis: Calculated (model output)
Used in atlas: Ch 7 LCOD calculator (CRF method); simulator cost per IT-kWh.
Used to derive: Levelised cost per IT-kWh.
Case | Annualised capex (₹ crore) | Opex (₹ crore) | IT energy (GWh) | LCOD (₹/IT-kWh) | Power cost (₹/IT-kWh) | Power share
A: 20 MW colo (12.6 MW average IT) | 1,222 × 0.1256 = 153.5 | 174 | 110.4 | 29.7 (~US$0.33) | 11.7 | 39%
B: 50 MW hyperscale, owner view | 2,120 × 0.1256 = 266.3 | 362.5 | 311.9 | 20.2 | 9.7 | 48%
C: AI campus, facility only | 7,400 × 0.1256 = 929.4 | ~921 | 700.8 | 26.4 | 8.45 | 32%
C: AI campus incl. GPUs | 929.4 + 26,620 × 0.2706 = 8,132 | 1187 | 700.8 | 133 (~US$1.48) | 8.45 | 6%
R7-T20 Cost per GPU-hour by utilisation
Source: Report 7 (full research report) · 3. Unit economics › 3.4 Cost per GPU-hour: TCO in India vs market prices
Note: Formula: GPU-hour cost at utilisation u = (capex + hosting + ops) ÷ (8,760 × u) + power per hour.
Data basis: Calculated (model output)
Used in atlas: Ch 7 GPU-hour calculator and chart.
Used to derive: GPU-hour cost at each utilisation.
₹/GPU-hour | Capex/hr (at 100%) | 100% | 80% | 60% | 40%
H100 (US$275k HGX → ₹36.5 lakh/GPU all-in; 1.4 kW) | 112.8 | 145 | 177 (US$1.97) | 232 | 343
H200 (~US$315k HGX → ₹41.8 lakh; 1.4 kW) | 129.1 | 161 | 198 | 259 | 384
B200 (US$450k HGX → ₹59.7 lakh; 2.0 kW) | 184.5 | 229 | 281 (US$3.12) | 368 | 545
GB300 NVL72, self-built campus (Case C) | 193.6 + 25 facility | 251 | 308 (US$3.42) | 404 | 598
R7-T21 GPU-hour market prices and break-even utilisation
Source: Report 7 (full research report) · 3. Unit economics › 3.4 Cost per GPU-hour: TCO in India vs market prices
Note: Market prices (Oct 2026 unless stated).
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 7 market-price table and dashed lines on GPU chart.
Used to derive: Break-even utilisation vs market prices.
Offer | ₹/GPU-hour | H100 breakeven utilisation vs our cost
IndiaAI L1 rate, high-end (H100-class); standard GPUs L1 ₹115.85. Users pay about ₹92 after a 40% subsidy, and Union Minister Ashwini Vaishnaw told the Lok Sabha that the average rate across the 34,381 GPUs onboarded from 14 providers is about ₹65/GPU-hr, with H100s at ₹92. | 150 | ~96% (5-year life); ~86% (6-year life)
JarvisLabs H100 | 217.89 | ~64%
Global OCPI-H100 index (2 Oct 2026): US$2.79 | ~251 | ~55%
E2E Networks H100 on-demand | 255.55 | ~54%
Yotta Shakti H100, dedicated (₹1,96,113/month) | ~269 | ~52%
Yotta Shakti H100 on-demand | 356 | ~39%
E2E H200 on-demand / 3-month+ commitment | 379.05 / 189.20 | H200: ~41% / ~84%
B200, global neocloud on-demand, US$3.70–6.00 | ~333–540 | B200: ~67% / ~41%
Hyperscaler H100 on-demand (AWS/Azure/GCP), US$6–12 | ~540–1,080 | Scarcity and convenience premium
R7-T22 Sensitivity analysis
Source: Report 7 (full research report) · 3. Unit economics › 3.5 Sensitivity analysis
Data basis: Calculated (model output)
Used in atlas: Ch 7 "What moves the colo's cost" tornado chart.
Used to derive: Which lever matters most.
Driver | Change | Case A (colo) | Case C (GB300 GPU-hour at 80%; base ₹308)
Tariff | ±₹1/kWh | LCOD ±₹1.5/IT-kWh. EBITDA ±₹16.6 crore if power is bundled; only ±₹1.7 crore if passed through at cost +10% | ±₹2.9/hr
Utilisation | A billed 70% vs 90%; C 60% / 40% | EBITDA −₹34 crore (yield 7.6%); LCOD ≈ ₹35 | ₹404 / ₹598
PUE | A 1.5→1.35; C 1.25→1.15 | Power −10% (≈₹12.9 crore/yr); LCOD −₹1.2 | −₹1.3/hr
Cost of capital | WACC 10% / 12% | LCOD ₹28.8 / ₹30.6 (annualised capex ₹143.6 / ₹163.6 crore) | ₹301 / ₹314
FX | ₹90 → ₹95/$ | Facility capex +~2% (≈₹1.1 crore/MW; imported share ~35–40%, estimate) | +₹13.5/hr
Import duties | Hypothetical 10% basic duty + surcharge on servers; or IGST not creditable | — | +₹26.6/hr; or +₹43.6/hr
GPU life | 4 / 6 years (H100 at 80%) | — | H100 ₹204 / ₹159 (base ₹177)
R7-T23 India vs US vs Singapore
Source: Report 7 (full research report) · 3. Unit economics › 3.6 Comparing models and markets
Note: India vs US vs Singapore (Houlihan Lokey using Cushman & Wakefield/CBRE; Turner & Townsend; CBRE)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 7 "India vs US vs Singapore" table.
Used to derive: India's thin margin vs peers.
Metric | India | US | Singapore
Build cost, Turner & Townsend (US$/W) | 6.64 (Mumbai) | 9.5–13.3 | 14.5
Development cost (US$M/MW) | 5.5–8.5 | 9–12 (Cushman & Wakefield 2026 US average US$17.6M all-in) | 9–14.5
Rent (US$/kW/month) | 80–100 | 160–225 (CBRE wholesale US$196) | 300–475 (retail-skewed)
Electricity (US$M/MW/yr) | 0.7–0.9 | ~1.22 | ~1.7
Total opex (US$M/MW/yr) | 1.0–1.2 | 5.0–5.5 as reported by Houlihan Lokey (looks inconsistent; treat with caution) | 2.0–2.4
Cap rate | 7.5–8.5% | 4.5–6.5% | 5.0–6.5%
Gross rent ÷ capex | ~15% | ~22% | very high (retail mix)
R7-T24 Colocation vs hyperscale vs AI neocloud
Source: Report 7 (full research report) · 3. Unit economics › 3.6 Comparing models and markets
Note: Colo vs hyperscale self-build vs AI neocloud
Data basis: Calculated (model output)
Used in atlas: Ch 7 returns comparison text.
Used to derive: Business-model risk profile.
| Colocation (A) | Hyperscale build-to-suit / self-build (B) | AI neocloud (C)
Capex intensity | ₹61 crore/MW | ₹42 crore/MW | ₹340 crore/MW
Revenue driver | ₹/kW rent + cross-connects | Long-term ₹/kW lease (or avoided rent) | ₹/GPU-hour × utilisation
Margin / return | 42% EBITDA; IRR ~9.5–13.5% depending on rent | 84% of rent; IRR ~14–15%; self-build 13–27% cheaper than leasing | 90% EBITDA but 5-year asset; IRR −ve to ~21%
Power share of cost | ~39% of LCOD | ~48% | ~6%
Key risk | Lease-up and rate pressure | Tenant concentration, pricing power | Utilisation, GPU price deflation, obsolescence

## R8
Report 8 · Green data centres
12 tables. Source line under each title; "Note" gives the context sentence from the report.
R8-T01 Twelve dimensions of a green data centre
Source: Report 8 (full research report) · 1. What is a "green data centre"? › 1.2 The twelve dimensions
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 8 "Twelve dimensions" grid.
Used to derive: Definition of green for India.
# | Dimension | Core metric(s) | What "green" looks like (India-tailored) | Why it matters
1 | Energy efficiency | PUE (ISO/IEC 30134-2) | ≤1.30 annualised (air); ≤1.20 (liquid-cooled AI) | Overhead energy is pure waste
2 | Carbon-free energy | REF, hourly CFE score, CUE | ≥70–80% hourly-matched CFE; CUE ≤0.3 kgCO₂/IT-kWh | India's grid factor 0.710 tCO₂/MWh makes power the dominant footprint
3 | Water | WUE (site), source WUE | ≤0.2 L/kWh freshwater; treated wastewater for any evaporative trim | Bengaluru water stress
4 | Embodied carbon (building) | kgCO₂e/m² or /MW (EN 15978-style LCA) | 30–40% below baseline via low-clinker concrete, recycled steel, hybrid timber | Grows in share as grids decarbonise
5 | IT hardware Scope 3 | kgCO₂e per server/GPU, lifecycle | Supplier EPDs/PCFs; extended refresh cycles | Now the largest share for hyperscalers
6 | Circularity | % IT assets reused/refurbished; e-waste diversion | ≥90% assets reused or recycled through authorised E-Waste (Management) Rules 2022 channels | Avoids manufacturing emissions and hazardous waste
7 | Heat reuse | ERF (ISO/IEC 30134-6), ERE | "Heat-reuse ready" design; absorption cooling or process heat where offtake exists | Turns waste into a product
8 | Refrigerants | GWP of charge, leakage rate | Low-GWP (HFO, natural refrigerants); chiller-less where possible | HFC leakage is a hidden Scope 1 source
9 | Land and biodiversity | Footprint, green cover, heat-island | Brownfield/industrial-park siting; native landscaping | Social licence, local heat
10 | Backup power | Diesel litres/yr, run-hours | HVO-ready gensets, BESS for short events, fuel cells long term | Diesel is local pollution and Scope 1
11 | Grid-friendliness | Demand response, flexibility MW | BESS/UPS grid services; schedulable AI training | Helps integrate renewables
12 | Social licence | Disclosure, local water/power impact, jobs | Public site-level dashboards; community water commitments | Without it, moratoria follow (Amsterdam, Dublin, Singapore 2019)
R8-T02 Green vs greenwashing: a quick test
Source: Report 8 (full research report) · 1. What is a "green data centre"? › 1.3 Green vs greenwashing: a quick test
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 8 "Spotting greenwashing" table.
Used to derive: Credibility test for claims.
Claim | Credible if… | Greenwashing red flag
"100% renewable" | Hourly or at least monthly matching, same grid region, additional (new) capacity, location-based Scope 2 also disclosed | Annual matching with unbundled RECs/I-RECs from old hydro elsewhere
"Carbon neutral" | Deep reductions first; removals (not avoidance offsets) for residuals | Cheap avoidance offsets netted against growing emissions
"PUE 1.2" | Annualised, measured at the utility meter boundary (ISO/IEC 30134-2 Category 2/3), at real load | Design PUE at 100% load, or a single cool-season month
"Water positive" | Site-level WUE disclosed; replenishment in the *same* basin | Global replenishment credits while a Bengaluru site draws borewells
"Green certified" | Operational certification with measured data | Design-stage label only, never re-verified
R8-T03 Core green metrics and formulas
Source: Report 8 (full research report) · 2. Metrics and standards › 2.1 Core metrics and formulas
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 8 metric definitions (reference).
Used to derive: CUE, ERF, CFE formulas.
Metric | Formula | Standard | Notes
PUE | Total facility energy ÷ IT equipment energy | ISO/IEC 30134-2 (The Green Grid, 2007) | Ideal 1.0; global weighted average 1.54 (Uptime 2025)
WUE | Annual site water (L) ÷ IT energy (kWh) | ISO/IEC 30134-9 | Karnataka policy uses this definition; the EU uses freshwater input
CUE | Total CO₂ from facility energy ÷ IT energy = grid EF × PUE (for grid-only supply) | ISO/IEC 30134-8 | Bengaluru grid-only at PUE 1.5: 0.710 × 1.5 = 1.07 kgCO₂/IT-kWh
ERF | Reused energy ÷ total facility energy | ISO/IEC 30134-6 | German EnEfG requires 10→20% for new sites
ERE | (Total energy – reused energy) ÷ IT energy | The Green Grid | Can be <1.0 with heat reuse
REF | Renewable energy ÷ total facility energy | ISO/IEC 30134-3 | Annual; does not capture timing
24/7 CFE score | Σ_h min(load_h, CFE supply_h) ÷ Σ_h load_h | Google/UN 24/7 CFE Compact methodology | The honest metric; Google fleet ≈65% (2025)
ITEEsv / ITEUsv | IT equipment energy efficiency / utilisation for servers | ISO/IEC 30134-4/-5 | Captures the compute side that PUE ignores
GEC | Green energy share of facility energy | ISO/IEC 30134 family (Japan-originated) | Similar in spirit to REF
R8-T04 Certifications compared
Source: Report 8 (full research report) · 2. Metrics and standards › 2.3 Certifications
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Reference only (certifications).
Used to derive: Which label to pursue.
Certification | Scope | Strength | Weakness
LEED (v4/v4.1 BD+C Data Centers; v5) | Building lifecycle; energy modelled against ASHRAE 90.4 | Globally recognised by tenants | Design-stage heavy; weak on hourly carbon
BREEAM | Building sustainability (UK/EU) | Strong on materials, ecology | Less used in India
IGBC Green Data Center Rating System (CII) | Design and Operational certification; enterprise, colo, hyperscale, edge, campuses | India-specific; aims to improve national average PUE by 20–25% | Voluntary; few disclosed operational ratings
GRIHA | Indian green building (TERI/MNRE) | Government projects | No DC-specific variant of note
BCA-IMDA Green Mark for DCs 2024 | Singapore | Platinum is now a licence condition | Singapore-specific
Uptime Tier + Sustainability assessments | Resilience; operational sustainability | Credible with enterprise buyers | Tier is resilience, not green
ISO 50001 / 14001 / 14064 | Energy management, environmental management, GHG verification | Process discipline; EnEfG requires EMS | Not a performance threshold
ENERGY STAR (US) | Top-quartile operational energy | Performance-based | US only
R8-T05 Indian standards and policy instruments
Source: Report 8 (full research report) · 2. Metrics and standards › 2.4 Indian standards and policy instruments
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 8 "Rules elsewhere" (India row) and Ch 9 central framework.
Used to derive: Indian policy instruments status.
Instrument | Status (Oct 2026) | Relevance
BEE / ECBC & Super ECBC | PUE benchmarks aligned with ECBC classes | Building-level; no binding DC PUE cap
MeitY tenders | AI cloud infrastructure tenders (since 2024) require PUE <1.35 | De facto public-procurement standard
TRAI | Recommendations on a regulatory framework for data centres (incl. green measures) | Advisory
IGBC Green DC | Voluntary design/operational certification | Market signalling
SEBI BRSR / BRSR Core | Listed companies disclose energy, water, emissions; assurance phased in | Covers listed operators and parents (Bharti, Adani, Reliance, Sify via US listing etc.)
Carbon Credit Trading Scheme | Compliance market: ~490 obligated entities in 7 industrial sectors; first CCC trading expected ~October 2026 | Data centres are *not* obligated entities; the offset mechanism and price signal matter
Draft National Data Centre Policy | Announced 2020; MeitY revived consultations (economic zones, single window, RE use) | No binding green thresholds yet
State DC policies | Karnataka 2026–31 (PUE/WUE reporting + incentives); UP 2026 (50% RE target for new DCs by 2030, green "booster" interest subsidy); others | States are leading on green conditions
Draft Climate Finance Taxonomy | DEA draft framework, May 2025 (comments to 25 June 2025); sectoral annexes pending | Inclusion of DCs with PUE/CFE criteria would unlock cheaper capital
R8-T06 Design levers with quantified savings
Source: Report 8 (full research report) · 3. Design levers with quantified savings
Note: The table below ranks levers for an Indian air-and-liquid hybrid facility. Savings are indicative ranges drawn from engineering practice and the series' prior reports. These are estimates, not measured Indian fleet data.
Data basis: Proxy / estimate
Used in atlas: Reference for green upgrade assumptions.
Used to derive: Savings per design lever.
Lever | Typical impact | Cost/complexity | India note
Site selection (climate, RE access, water, grid) | 0.05–0.15 PUE; large water and carbon effects | Low if early | Bengaluru's mild, elevated climate beats Chennai/Mumbai for free cooling; Hoskote park pairs Pavagada solar + 60 MLD treated water
Hot/cold-aisle containment | 10–20% cooling energy | Low | Table stakes
Raised supply air temperature (ASHRAE recommended 18–27 °C) | 2–4% chiller energy per °C | Low | Germany will require 27 °C inlet from 2028
Free cooling / economisers, dry coolers | 0.05–0.15 PUE in Bengaluru | Medium | Many hours below 24 °C wet-bulb
Direct-to-chip liquid cooling (DLC) | Removes ~70–80% of heat with warm water (30–45 °C); enables PUE 1.1–1.2 | Medium-high | Essential for 50–130 kW AI racks
Immersion cooling | PUE ~1.03–1.1; no fans | High; ecosystem immature | Niche/edge
High-efficiency UPS / eco-mode | 2–4% of facility energy | Low-medium | Eco-mode at 99% efficiency vs ~94–96% double-conversion
Low-loss transformers, 415 V / higher-voltage distribution; 800 VDC for AI racks | 1–3% | Medium | 800 VDC is emerging with next-generation GPU racks
Lithium-ion UPS batteries | Smaller footprint, longer life | Medium | Fire-safety design essential
Server utilisation, virtualisation, consolidation | Can halve IT energy per workload | Low (software) | The biggest lever that PUE does not see
Efficient chips (ARM, accelerators), power capping | 10–30% per workload | Medium | Procurement criterion: SS 715-type standards
AI model efficiency (distillation, quantisation, batching) | Large; Google reports a 33× fall in median Gemini prompt energy over one year (self-reported, unverified) | Software | Demand-side efficiency matters most for AI
AI-driven cooling optimisation, DCIM, digital twins | 5–15% cooling energy | Low-medium | Quick win on existing Indian stock
Carbon-aware scheduling | Shifts flexible loads to solar hours | Low | India's solar-heavy midday supply favours daytime batch/training
Low-carbon materials (low-clinker concrete, recycled steel, hybrid timber) | Microsoft: hybrid mass timber cut embodied carbon an estimated 35% vs steel and 65% vs precast concrete; Google cites up to 40% from low-carbon materials | Medium | Fly-ash/slag cements are abundant in India
Cool roofs, passive design | Small energy effect; reduces heat island | Low | Supports social licence
Treated wastewater (TTW) for cooling | Cuts freshwater to near zero | Medium (treatment plant) | Karnataka reimburses treated-water charges
R8-T07 Renewable procurement options in India
Source: Report 8 (full research report) · 4. Renewable and carbon-free energy procurement › 4.1 Procurement options in India
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 8 "Buying clean power in India" table; simulator RE price.
Used to derive: Landed cost of clean power routes.
Route | How it works | Typical landed cost (est.) | Pros | Cons
On-site rooftop solar | Behind-the-meter | ₹3–4/kWh | No OA charges | Meets <2–5% of a DC's load (density)
Group captive | Consumer holds ≥26% equity and consumes ≥51% | ₹5.5–7/kWh | Exempt from cross-subsidy and additional surcharges | Equity lock-in; state rules vary
Third-party open access PPA | Wheeled RE under state OA rules | ₹6.5–8/kWh | Flexible | Surcharges, banking limits, regulatory risk
Green Energy Open Access (2022 Rules) | ≥100 kW consumers; faster approvals, capped charges | Varies | National framework | Karnataka High Court struck down the state application; KERC issued new OA Regulations 2025
ISTS hybrid PPAs | Inter-state solar-wind(-storage) | ₹5–6.5/kWh at bus + charges | Better hourly profile | Transmission waiver phase-down
SECI RTC/FDRE auctions | Firm, dispatchable RE (prior report: ₹5.25/kWh) | ~₹5.25 + delivery | High CFE share | Mainly for discoms; replicable bilaterally
State green tariffs | Discom supplies RE at a premium | Tariff + premium | Simple | Additionality unclear
RECs / I-RECs | Unbundled certificates | ₹0.1–0.3/kWh | Cheap | Weakest claim; Microsoft has paused non-additional unbundled RECs
BESS / pumped storage | Firming | Adds ₹1.5–3/kWh to firmed supply | Lifts hourly CFE | Capex
Nuclear | Future PPAs | n/a in India today | 24/7 CFE | India's SHANTI Act (December 2025) opened private participation; ₹20,000 crore Nuclear Energy Mission targets ≥5 indigenous SMRs by 2033; draft rules August 2026
R8-T08 Indian operator green snapshot
Source: Report 8 (full research report) · 4. Renewable and carbon-free energy procurement › 4.4 Indian operator snapshot
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 8 "Indian operators" table.
Used to derive: Operator green credentials.
Operator | Green credentials (latest disclosed) | Assessment
Nxtra by Airtel | 49% RE in core DCs (FY25); 482,800 MWh RE contracted (3× FY21); PUE down 10% vs FY21; first Indian DC in RE100 (June 2024); 125.65 MW ISTS hybrid with AMPIN (205,167 MWh/yr); FY26 report targets 70% RE | Best-disclosed Indian operator; still annual matching
AdaniConneX | 1 GW platform; US$875m sustainability-linked loan (up to US$1.44bn) with KPIs on energy efficiency, RE adoption and safety (first SLL in Indian DC sector, ING-led); partner in Google Vizag | Strong financing signal; site PUE/CFE data limited
Google–AdaniConneX–Nxtra, Vizag | US$15bn (2026–30), ~1 GW across three campuses; ground broken 28 April 2026; new RE + storage by Adani | Reports conflict on whether power comes from new Andhra Pradesh generation or Khavda (Gujarat); the hourly-matching design is undisclosed
Sify | >231 MW RE contracted; AI racks up to 200 kW | Good procurement; limited PUE disclosure
CtrlS | Captive solar (Nagpur) for Mumbai; NTPC Green partnership | Procurement-led
Yotta | Green tariff via Hiranandani group utility TUCO (hydro, biogas) | Novel structure; additionality unclear
Reliance–Meta, Jamnagar | 168 MW AI DC announced June 2026, "supported by renewable energy" | Too early to assess
STT GDC India, NTT India, AWS/Microsoft India | RE PPAs announced in several states | *Site-level figures not re-verified this cycle*
R8-T09 Global benchmarks: Google, Microsoft and others
Source: Report 8 (full research report) · 5. Global benchmarks and the AI problem
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 8 headline (+18% / +25% emissions); Ch 5 text.
Used to derive: Limits of annual RE matching.
Company | Efficiency | Clean energy | Emissions trend | Water / other
Google | Fleet PUE 1.09 (2025); 83% less overhead than the 1.54 industry average | ~65% hourly CFE; 12 GW new contracts; 100% annual match (9th year) | Ambition-based footprint +18% to ~14.5 Mt; Scope 3 +25%; DC construction ~2.3 Mt; electricity +37% | Target 24/7 CFE and 50% cut by 2030
Microsoft | n/a fleet PUE | 40 GW contracted (19 GW online); 100% annual match | FY25 20.29 Mt vs 12.88 Mt FY20 (+~58% market-based; Stand.earth estimates ~80% gross); +25% YoY; Scope 2 now 13% of total after dropping unbundled RECs | Owned-DC WUE 0.27 L/kWh; zero-water-for-cooling design (from August 2024) avoids >125 million L/yr per DC; mass-timber DCs
Meta, AWS, Equinix, Digital Realty, NTT, Iron Mountain, Apple | 100% annual RE matching widely claimed; AWS "water positive by 2030"; Iron Mountain an early 24/7 CFE adopter | — | Mostly rising absolute emissions with AI | *Figures not re-verified this cycle*
R8-T10 Green upgrade worked example: assumptions
Source: Report 8 (full research report) · 6. Economics of going green: a 20 MW Bengaluru colocation worked example › 6.1 Assumptions (flagged estimates)
Data basis: Proxy / estimate
Used in atlas: Ch 8 green upgrade calculator defaults.
Used to derive: Inputs for the 20 MW green case.
Parameter | Baseline | Green design | Source/basis
IT capacity | 20 MW | 20 MW | —
Average IT utilisation | 70% → 14 MW avg | Same | Estimate
Annual IT energy | 14 × 8,760 = 122.64 GWh | Same | Calc
PUE | 1.5 | 1.25 | Indian average vs green target
Facility energy | 183.96 GWh | 153.30 GWh | Calc
Power source | 100% grid | 80% RTC RE (group captive/OA), 20% grid | —
Grid all-in tariff | ₹8.0/kWh | ₹8.0/kWh | Estimate for HT commercial incl. demand charges and duty
RE landed cost | — | ₹7.25/kWh (central); range ₹6.5–8.5 | SECI RTC ₹5.25 + OA charges/banking (estimate)
Grid emission factor | 0.710 tCO₂/MWh | 0.71 | CEA (prior report)
Cooling / WUE | Evaporative towers, 1.8 L/kWh freshwater | Dry coolers + DLC-ready, TTW adiabatic trim; 0.2 L/kWh freshwater | Estimate
Base capex | ₹56 crore/MW → ₹1,120 crore | + green premium | Prior unit-economics report
Green capex premium | — | ₹60 crore (~5.4%) | Estimate: efficient chillers/dry coolers, containment, eco-mode UPS, TTW plant, DCIM/digital twin, IGBC, low-carbon concrete, rooftop PV
R8-T11 Marginal abatement cost by package
Source: Report 8 (full research report) · 6. Economics of going green: a 20 MW Bengaluru colocation worked example › 6.3 Marginal abatement cost (MAC)
Note: MAC = (annualised capex + Δopex) ÷ tCO₂ abated
Data basis: Calculated (model output)
Used in atlas: Ch 8 "Abatement cost by measure" chart; Key numbers.
Used to derive: Marginal abatement cost per package.
Package | Net annual cost (₹ crore) | tCO₂ abated/yr | MAC (₹/tCO₂)
Efficiency + water (PUE 1.5→1.25, dry/TTW) | 7.9 – 24.5 – 1.8 = –18.4 | 21800 | ≈ –₹8,450
RE at ₹0.75/kWh discount | –9.2 | 87100 | ≈ –₹1,060
RE at ₹0.50/kWh premium (adverse OA case) | +6.1 | 87100 | ≈ +₹700
Full package (central case) | –27.6 | 108800 | ≈ –₹2,540
R8-T12 Green data-centre maturity model (India-calibrated)
Source: Report 8 (full research report) · 8. Green Data Centre maturity model (India-calibrated)
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 8 maturity self-check radar.
Used to derive: Maturity level per dimension.
Dimension | L1: Basic | L2: Managed | L3: Efficient | L4: Leading | L5: Regenerative
Energy (annual PUE, measured) | >1.7 or unmeasured | 1.5–1.7 | 1.35–1.5 | 1.2–1.35 | ≤1.20 (air) / ≤1.15 (liquid)
Carbon (hourly CFE / CUE) | Grid only; CUE >1.0 | Annual RECs; REF <50% | REF 50–80% via PPAs | ≥70% hourly CFE; CUE ≤0.3 | ≥90% hourly CFE, additional; location-based disclosed
Water (freshwater WUE, L/kWh) | >2.0 or unmeasured | 1.3–2.0 | 0.7–1.3 | 0.2–0.7; TTW | <0.2; zero freshwater for cooling; basin replenishment
Materials (embodied) | No LCA | LCA done | 10–20% below baseline | 30–40% below; EPDs required | >40% below; hybrid timber; low-clinker
Circularity | Ad hoc disposal | Authorised e-waste recycler | ≥50% assets reused/refurbished | ≥90% reuse/recycle; extended lifecycles | Closed-loop component recovery; supplier take-back
Heat | Rejected | Assessed | Heat-reuse ready (EU definition) | ERF 2–10% (absorption cooling/process heat) | ERF >10% with contracted offtaker
Backup | Diesel, unmonitored | Diesel run-hours tracked | HVO-ready, BESS for short events | BESS + HVO; diesel <20 h/yr | Fuel cells/zero-emission backup
Transparency | None | Annual report (BRSR) | Site-level PUE/WUE published | Third-party assured PUE/WUE/CFE; Scope 3 | Real-time public dashboards; hourly CFE

## R9
Report 9 · State policies
4 tables. Source line under each title; "Note" gives the context sentence from the report.
R9-T01 Central framework instruments
Source: Report 9 (full research report) · Part A — Central Framework
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 9 "The central framework" table.
Used to derive: National levers vs state levers.
Instrument | Status (Oct 2026) | What it does / implication
Draft National Data Centre Policy (MeitY) | Released 5 Nov 2020 for comments (deadline extended to 30 Nov 2020); never notified. MeitY has resumed industry consultations; one market-research release describes a "finalised draft" with up to 20-year conditional tax exemptions, but this is unverified. | Proposed four Data Centre Economic Zones (DCEZs), single-window clearance, infrastructure status, and support for indigenous servers, storage, networking and cooling. Lacked enforceable mandates. Treat "imminent" claims sceptically: it has been pending for nearly six years.
Infrastructure status | In the Harmonised Master List of Infrastructure sub-sectors since 11 Oct 2022 | Applies to data centres of at least 5 MW IT load. Eases long-tenor bank and ECB financing. The Finance Act 2026 tax-holiday definition does not use the 5 MW threshold, so a facility can qualify under one and not the other.
Union Budget 2026–27 (1 Feb 2026) | Enacted in the Finance Act; subordinate notifications on qualifying criteria still pending (Norton Rose Fulbright) | Tax holiday until 31 March 2047 for foreign companies that provide cloud services globally using India-based data-centre services. Indian customers must be served through an Indian reseller. A 15% cost-plus safe harbour applies to related Indian data-centre service providers, and IT services generally move to a 15.5% safe harbour. This is the most important central incentive, but it benefits foreign cloud firms and Indian colocation operators indirectly and has no green conditions.
DPDP Act 2023 / DPDP Rules 2025 | Rules notified 14 Nov 2025 | "Soft localisation": cross-border transfers are allowed unless the government blacklists a country. Demand for local hosting comes more from sector rules — RBI payment-data localisation (all payment data stored in India) and the SEBI Cloud Framework 2023 (data and logs on Indian servers) — than from the DPDP regime itself.
MeitY cloud empanelment (GI Cloud / MeghRaj) | Ongoing | Government workloads must use MeitY-empanelled cloud service providers hosted in audited Indian data centres. This creates steady sovereign demand, especially for Tier III facilities. *(Not re-verified in this research.)*
IndiaAI Mission | Ongoing | Subsidised GPU compute procured from private data-centre operators. It shapes demand for high-density, liquid-cooled capacity. *(Not re-verified in this research.)*
Green Energy Open Access Rules 2022 (MoP) | In force | Lowered the open-access threshold to 100 kW and capped additional surcharges, enabling corporate renewable procurement. CEEW stakeholders still name high cross-subsidy surcharge (CSS) and additional surcharge, inconsistent banking rules and sudden withdrawal of waivers as the main barriers.
ISTS charges waiver | Being phased down for projects commissioned after mid-2025 *(general knowledge, not re-verified)* | Makes inter-state renewable PPAs dearer over time, so state-level wheeling and banking concessions matter more.
TRAI recommendations on data centres, CDNs and interconnect exchanges | Issued Nov 2022 (often cited as 2023); not implemented by statute | Recommended a legal framework, a single-window system, a data-centre-specific building-code category and incentives. Industry still asks for a National Building Code category for data centres.
CEA/MoP draft guidance on power for data centres | *Not verified in this research.* | Flagged as a gap: no publicly verified central power-supply standard for data centres was found.
SEZ route | Available | Data centres can be set up in IT/ITeS SEZs, for example the 2.7 ha SEZ portion of RackBank's Nava Raipur park. The Budget's IFSC tax-holiday extension (20 of 25 years) helps GIFT City-type locations.
GST | Standard rate on data-centre/colocation services *(not re-verified)* | States compete through SGST reimbursement, which is the reason "net SGST reimbursement" appears in almost every policy.
R9-T02 Telangana named projects
Source: Report 9 (full research report) · Part B — State-by-State Deep Dive › 4. Telangana — the inland AI challenger
Note: Implementation: According to Knight Frank India's "India Data Centre Market Update 2025", Hyderabad live capacity rose from 60.9 MW (2022) to 151.4 MW (end-2025), with a 1.9 GW committed pipeline, second only to Mumbai. AWS, which runs three availability zones in the city, holds 46% of live IT capacity. Named projects:
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 9 Telangana detail; Ch 10 demand context.
Used to derive: Hyderabad pipeline evidence.
Project | Size / investment | Details
AWS | ₹60,000 crore | Foundation stone July 2026
TCS HyperVault | Up to 1 GW, up to ₹70,000 crore | 264 acres, Future City; announced September 2026
CtrlS | 400 MW, ₹10,000 crore | MoU 2025
NTT DATA–Neysa | 400 MW, ₹10,500 crore | MoU 2025
Microsoft India South Central region | — | Launched 2026
R9-T03 Master comparison of state policies
Source: Report 9 (full research report) · Part C — Master Comparison Table
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 9 policy register table, map detail panel and validity chart; simulator incentives.
Used to derive: Incentives and green conditions by state.
State | Instrument / status | Target | Capex / interest | Power | Land / stamp | Green conditions | Validity
Maharashtra | IT/ITeS 2023 + IGDCP GRs (Oct 2024; Jun 2026) — active | 20 parks; 30–40 GW by 2047 | IPS 75% of fixed capital investment (≥₹60k cr); 4% interest, ₹25 cr/yr | ED 20 yrs; ₹1/unit 10–20 yrs | Stamp duty 100% (IGDCP); any-zone siting | 51% RE (cut from 100%) | IT policy to 2028; GR open-ended
Tamil Nadu | DC Policy 2021 — lapsed 31.3.2026 | — | — | Electricity tax 100%, 5 yrs | Stamp duty 50–100%; 50% land (Cat C) | ≥30% RE eligibility | Expired
Karnataka | Sustainable DC Policy 2026–31 — approved Sept 2026 | 1 GW; ₹1,300.45 cr outlay | Capital subsidy; R&D 50% up to ₹15 cr | ED exemption; wheeling reimbursement | Parks on 30+30-yr lease | PUE/WUE reporting; ₹20 cr PUE; WUE & treated-water reimbursement | 2031
Telangana | DC Policy 2016 + bespoke deals | ~5 GW by 2029–30 (stated) | Lease rental 25%; R&D | Power incentives; dual grid | Land subsidy (govt land); 50% building fee | None | Legacy
Andhra Pradesh | DC Policy 4.0, G.O.Ms.6 (14.11.2024) | 200 MW–1 GW (policy); 6.5 GW (claimed) | 100% SGST on capital goods or 10% P&M; mega >50 MW/>₹5k cr bespoke | Industrial tariff; T&W case-by-case | Stamp duty 100% first sale; land discount (mega) | Seawater cooling; "70% RE" (stated, not notified) | 2029 or new policy
Uttar Pradesh | DC Policy 2026 (replaced 2021) | +2 GW; ₹2 lakh cr | 7% up to ₹20 cr (+₹5 cr AI); 60% interest (+₹10 cr AI) | ED 10 yrs; T&W relief; dual grid | 25–50% land; stamp duty 100% | PUE/green-cert booster; 50% RE by 2030 | ~2031 (assumed)
Gujarat | DC Policy 2026–29 + IT/ITeS 2022–27 | 7.5 GW; ₹6 lakh cr | 2.5% capex (Dholera); 4% interest, ₹25 cr/yr; cap 75% of fixed capital investment | ₹1/unit 20 yrs; ED 20 yrs | Stamp duty & registration 100% | 51% RE | 2029
Haryana | DC Policy 2022 | 115–120 DCs; ₹7,500 cr | Net SGST 50–75%, 10 yrs | ED 20 yrs; power bill ≤25% of SGST | Stamp duty 100% | None | ~2029 (verify)
West Bengal | DC Policy 2021 (No. 490-ITE) | 400 MW by 2025 | — | ED 5 yrs; dual grid | Stamp duty & registration 100% | Captive water treatment | Lapsing ~Sept 2026
Odisha | DC Policy 2022 | — | 20% up to ₹25 cr; 5% interest | 30% bill 5 yrs; ED 10 yrs; captive-RE T&W 100% | Stamp duty 100/50% | Clean-green subsidy; carbon framing | Verify
Rajasthan | DC Policy 2025 | 300 MW; ₹20,000 cr | Asset-creation ₹10–20 cr/yr; 5% interest | Banking/T&W 100% waiver; ED 7 yrs | Stamp duty, conversion exemptions | ZLD, recycling, green-building; green incentive ₹12.5 cr | ~2030
Madhya Pradesh | IT/ITeS & ESDM 2023 | — | 25% up to ₹125 cr (anchors) | Tariff rebate; ED | Stamp reimbursement | Green DC support (vague) | ~2028
Bihar | IT Policy 2024 | — | 30% up to ₹30 cr or interest | 25% tariff 5 yrs | Lease subsidy | None | ~2029
R9-T04 State attractiveness index
Source: Report 9 (full research report) · Part D — Attractiveness Index
Note: Methodology (author's weighted judgment, 0–10 per factor). Weights: power cost and reliability 25%; renewable access 15%; connectivity (subsea/IX/fibre) 15%; incentives 15%; land and park readiness 10%; water security 10%; regulatory ease and policy stability 10%. Scores reflect the evidence above, not a published index.
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 9 attractiveness index (sliders) and map colouring; Ch 10 policy factor.
Used to derive: Weighted state ranking.
Rank | State | Power | RE | Connectivity | Incentives | Land | Water | Regulatory | Weighted
1 | Maharashtra | 8 | 6 | 10 | 8 | 6 | 6 | 8 | 7.8
2 | Telangana | 8 | 7 | 6 | 7 | 9 | 6 | 7 | 7.2
3 | Andhra Pradesh | 7 | 9 | 7 | 9 | 7 | 5 | 6 | 7.3
4 | Tamil Nadu | 7 | 8 | 10 | 4 | 6 | 4 | 5 | 6.8
5 | Uttar Pradesh | 7 | 5 | 6 | 8 | 7 | 6 | 8 | 6.7
6 | Gujarat | 7 | 9 | 4 | 9 | 8 | 4 | 7 | 6.8
7 | Karnataka | 6 | 8 | 5 | 6 | 6 | 4 | 7 | 6
8 | Haryana | 6 | 4 | 6 | 7 | 4 | 4 | 7 | 5.5
9 | West Bengal | 6 | 4 | 6 | 5 | 6 | 7 | 4 | 5.4
10 | Odisha | 7 | 6 | 4 | 7 | 7 | 7 | 6 | 6.2
11 | Rajasthan | 6 | 10 | 2 | 8 | 8 | 2 | 6 | 5.9
12 | Madhya Pradesh | 6 | 6 | 3 | 7 | 7 | 5 | 6 | 5.6

## R10
Report 10 · Where to build
22 tables. Source line under each title; "Note" gives the context sentence from the report.
R10-T01 Market context: capacity by city, H1 2026
Source: Report 10 (Part 10 research report) · Key Findings
Note: 1. Market context (reported). Cushman & Wakefield's H1 2026 update puts operational capacity at 1,789 MW across seven markets, with 3,860 MW more due by 2030 (509 MW under construction and 3,351 MW planned). By city:
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 10 context; Ch 1/9 city capacity.
Used to derive: Market size and pipeline by city.
Market | Operational (MW) | Upcoming (MW)
Mumbai | 890 | 1726
Chennai | 214 | 368
Delhi NCR | 183 | 387
Bengaluru | 162 | 100
Hyderabad | 151 | 710
Pune | 133 | 258
Kolkata | 22 | 84
R10-T02 Effective tariff by state at 80% load factor
Source: Report 10 (Part 10 research report) · Key Findings
Note: 6. Tariffs vary by about ₹2.7/kWh across states. Over 20 years at 100 MW, that gap is worth more than any capex incentive. Effective cost is computed at 80% load factor, as energy charge + demand charge ÷ 584 h:
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 power score (tariff half); city detail panel.
Used to derive: Tariff score = 10 × (8.70 − x) ÷ (8.70 − 5.96).
State | Tariff basis | Effective ₹/kWh
Odisha | EHT, ₹250/kVA, 580/470 paise slabs | ≈ ₹5.96 (cheapest)
Kerala | EHT 220 kV ₹5.55, demand charge estimated | ≈ ₹6.23
Haryana | 132 kV | ≈ ₹7.1
Uttar Pradesh | NIDP HV-2 | ≈ ₹7.41
Telangana | 132 kV | ≈ ₹7.51
Karnataka | HT-2(a) | ≈ ₹7.61
Madhya Pradesh | HV-3 132 kV | ≈ ₹8.2
Tamil Nadu | HT-I | ≈ ₹8.54
Maharashtra | HT-I(A) | ≈ ₹8.7
R10-T03 Factor weights by use case
Source: Report 10 (Part 10 research report) · Method
Note: Weights.
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 10 weight presets (balanced, AI, interconnection, sustainability).
Used to derive: Use-case rankings.
Factor | Default | AI campus | Interconnect | Sustainability
Power | 25 | 40 | 15 | 20 (RE-access score replaces tariff)
Connectivity | 15 | 5 | 30 | 5
Latency | 10 | 5 | 20 | 5
Water | 15 | 15 | 5 | 30
Climate | 5 | 5 | 0 | 15
Hazards | 10 | 10 | 10 | 10
Land | 5 | 10 | 2 | 5
Policy | 10 | 7 | 5 | 5
Demand/talent | 5 | 3 | 13 | 5
R10-T04 Inter-hub distances and latency
Source: Report 10 (Part 10 research report) · Method
Note: Latency formula. RTT (ms) ≈ 2 × d × 1.4 ÷ 200 = 0.014 × d (km). Inter-hub baselines:
Data basis: Calculated (model output)
Used in atlas: Ch 10 latency formula drawer.
Used to derive: RTT = 0.014 × km.
Route | Distance | RTT
Mumbai–Delhi | 1,150 km | 16.1 ms
Mumbai–Chennai | 1,030 km | 14.4 ms
Mumbai–Bengaluru | 845 km | 11.8 ms
Delhi–Chennai | 1,760 km | 24.6 ms
Delhi–Bengaluru | 1,740 km | 24.4 ms
Chennai–Bengaluru | 290 km | 4.1 ms
R10-T05 Latency table: great-circle km to four hubs and mean RTT
Source: Report 10 (Part 10 research report) · Latency table (great-circle km to Mumbai / Delhi / Chennai / Bengaluru → mean RTT)
Data basis: Calculated (model output)
Used in atlas: Ch 10 latency factor (recomputed in the atlas with haversine).
Used to derive: Latency score per city.
City | M | D | C | B | Mean RTT (ms) | Score
Anantapur | 705 | 1547 | 338 | 190 | 9.7 | 10
Bengaluru / Hoskote | 845 | 1740 | 290 | 0–25 | 10.1–10.2 | 10.0–9.9
Hyderabad | 620 | 1250 | 520 | 500 | 10.1 | 10
Hosur | 850 | 1760 | 260 | 35 | 10.2 | 9.9
Pune | 120 | 1170 | 910 | 735 | 10.3 | 9.9
Sri City | 980 | 1700 | 55 | 250 | 10.4 | 9.8
Navi Mumbai | 15 | 1150 | 1020 | 835 | 10.6 | 9.7
Chennai | 0–1,030 | 1760 | 0 | 290 | 10.8 | 9.6
Nashik | 140 | 1040 | 1040 | 900 | 10.9 | 9.6
Amaravati | 856 | 1385 | 381 | 504 | 10.9 | 9.6
Mysuru | 820 | 1810 | 385 | 125 | 11 | 9.5
Goa (Verna) | 428 | 1508 | 735 | 479 | 11 | 9.4
Warangal | 760 | 1180 | 560 | 640 | 11 | 9.5
Mangaluru | 710 | 1760 | 580 | 300 | 11.7 | 9
Nagpur | 685 | 860 | 925 | 900 | 11.8 | 9
Indore | 510 | 667 | 1167 | 1098 | 12.1 | 8.8
Bhopal | 663 | 594 | 1170 | 1142 | 12.5 | 8.5
Coimbatore | 1000 | 1960 | 430 | 225 | 12.7 | 8.4
Dholera | 360 | 850 | 1330 | 1170 | 13 | 8.2
Ahmedabad / GIFT | 440 | 775 | 1380 | 1230 | 13.4 | 8
Nava Raipur | 957 | 953 | 913 | 1013 | 13.4 | 8
Visakhapatnam | 1100 | 1340 | 610 | 800 | 13.5 | 7.9
Kochi | 1080 | 2060 | 545 | 355 | 14.1 | 7.5
Jamnagar / Jaipur | 480 / 920 | 950 / 240 | 1,530 / 1,600 | 1,350 / 1,560 | 15.1 | 6.9
Jharsuguda | 1201 | 1022 | 1051 | 1197 | 15.6 | 6.5
Thoothukudi | 1270 | 2200 | 530 | 470 | 15.6 | 6.6
Thiruvananthapuram | 1200 | 2210 | 620 | 490 | 15.8 | 6.5
Jodhpur | 795 | 540 | 1700 | 1570 | 16.1 | 6.3
Delhi / Noida / Gurugram / Greater Noida | 1,130–1,150 | 0–60 | 1,720–1,760 | 1,700–1,740 | 16.2–16.3 | 6.1
Lucknow / Kanpur | 1190 | 420 | 1550 | 1580 | 16.6 | 6
Bhubaneswar | 1365 | 1274 | 996 | 1195 | 16.9 | 5.8
Ranchi | 1380 | 1006 | 1257 | 1410 | 17.7 | 5.3
Patna / Dehradun | 1,457 / 1,350 | 860 / 205 | 1,479 / 1,930 | 1,607 / 1,926 | 18.9 | 4.5
Digha / Kharagpur | 1552 | 1297 | 1213 | 1412 | 19.2 | 4.3
Mohali / Baddi | 1380 | 240 | 1990 | 1960 | 19.5 | 4.2
Kolkata | 1650 | 1300 | 1360 | 1560 | 20.5 | 3.5
Guwahati | 2079 | 1461 | 1880 | 2078 | 26.2 | 0
R10-T06 State shortlist: Maharashtra
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Maharashtra
Note: Land [R]: MIDC TTC base rate is ₹31,390/m² (≈ ₹12.7 cr/acre). The market rate is ₹45,000–60,000/m² or more, and STT paid ₹282 cr for 14,093 m² including a building in May 2026. Taloja is ₹12,100/m² (≈ ₹4.9 cr/acre).
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City (lat, long; district) | EHV node [E] | Water | Hazard (zone/other) | Design DB/WB °C; FC h [E] | Demand | Scores | Total | Tier
1 | Navi Mumbai – TTC/Mahape/Rabale (19.03, 73.03; Thane/Raigad) | 400 kV Kharghar / Kalwa, 5–15 km | Dam-fed municipal supply plus STP; Thane district not over-exploited [E] | III; monsoon flooding | 35/26; ~50 | Mumbai 890 MW op / 1,726 MW upcoming [R] | 4.5/10/9.7/7/2/5/2/8/10 | 6.6 | A
2 | Pune – Chakan/Talegaon/Hinjewadi (18.52, 73.86; Pune) | 400 kV Chakan / Lonikand, 10–20 km | Haveli semi-critical [E] | III | 38/25; ~1,500 | 133 MW op / 258 MW upcoming [R] | 4.0/7/9.9/6/5/7/5/8/8 | 6.3 | A
3 | Nagpur – MIHAN/Butibori (21.15, 79.09; Nagpur) | 400 kV Koradi ~25 km; 220 kV Butibori <10 km | Safe [E] | II; heat (44 °C) | 44/27; ~1,500 | NIXI node; small DC base | 4.0/5/9.0/7/5/9/8/8/4 | 6.3 | A
4 | Nashik (20.00, 73.79; Nashik) | 400 kV Eklahare, 10–20 km | Safe [E] | III | 39/25; ~1,800 | NIXI node | 3.0/5/9.6/7/6/7/7/8/3 | 5.8 | B
R10-T07 State shortlist: Tamil Nadu
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Tamil Nadu
Note: Tariff [R]: TNERC T.O. No. 6 of 2025 sets HT-I at ₹7.50/kWh and ₹608/kVA/month, with no revision announced for 2026. Effective ≈ ₹8.54.
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City | EHV node [E] | Water | Hazard | DB/WB; FC h [E] | Demand | Scores | Total | Tier
1 | Hosur (12.74, 77.83; Krishnagiri) | 400 kV Hosur ~10 km | Semi-critical to over-exploited [E] | II | 35/24; ~2,500 | Bengaluru spill-over | 3.8/6/9.9/4/6/9/7/4/6 | 5.7 | B
2 | Chennai – Ambattur/Sriperumbudur/Siruseri (13.08, 80.27; Chennai/Tiruvallur/Kancheepuram/Chengalpattu) | 400 kV Alamathy / Sriperumbudur, 5–20 km | District 127.47%, 13/16 taluks over-exploited [R]; TTRO/desal available → conditional | III; floods 2015/2023; cyclone | 38.5/28.5; ~0 | 214 MW op / 368 MW upcoming; 8 cables [R] | 4.3/10/9.6/3/1/4/4/4/9 | 5.5 | B (A for colo)
3 | Coimbatore (11.02, 76.96; Coimbatore) | 400 kV Arasur ~20 km | Mixed [E] | III | 37/25; ~400 | NIXI node; wind belt | 4.3/5/8.4/5/5/7/7/4/6 | 5.4 | B
4 | Thoothukudi (8.76, 78.13; Thoothukudi) | 765/400 kV Tuticorin PS, 15–25 km | Seawater/desal option | II; coastal cyclone | 38/28; ~0 | BSNL CLS (Sri Lanka) + NIXI | 4.8/7/6.6/5/1/6/8/4/2 | 5.2 | C
R10-T08 State shortlist: Karnataka
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Karnataka
Note: Tariff [R/E]: KERC Order of 27 March 2025 sets HT-2(a) at about ₹700 paise/kWh for FY27 and about ₹355/kVA. The subagent could not confirm the exact row. Data centres are billed as industrial with a DoIT certificate. Effective ≈ ₹7.61.
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City | EHV node [E] | Water | Hazard | DB/WB; FC h [E] | Demand | Scores | Total | Tier
1 | Mysuru (12.30, 76.64; Mysuru) | 400 kV Mysuru (Kadakola), ~15 km | Cauvery-fed; safe to semi-critical [E] | II | 35/24; ~2,000 | Nascent | 5.0/4/9.5/7/8/9/7/8/3 | 6.5 | A
2 | Hoskote (13.07, 77.80; Bengaluru Rural) | 400 kV Hoody ~20 km | Hosakote over-exploited [R] → conditional | II | 34.5/23.5; ~2,200 | Hyperscale land bank | 5.5/6/9.9/2/8/9/6/8/8 | 6.4 | A (conditional)
3 | Bengaluru core – Whitefield/EC (12.97, 77.59; Bengaluru Urban) | 400 kV Hoody / Somanahalli, 5–25 km | All 6 units over-exploited; East 395% [R] → conditional | II; urban flooding | 34.5/23.5; ~2,000 | 162 MW op / 100 MW upcoming [R] | 5.0/7/10/1/8/8/3/8/10 | 6.1 | B (conditional)
4 | Mangaluru (12.91, 74.86; Dakshina Kannada) | 220 kV local <15 km; 400 kV ~50 km | High rainfall; safe [E] | III; monsoon | 34/27; ~0 | Coastal edge | 5.0/6/9.0/7/2/6/6/8/3 | 6.1 | B
R10-T09 State shortlist: Telangana
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Telangana
Note: Tariff [R]: TGERC FY2026-27 RST order, unchanged from FY26, sets HT-I(A) at ₹6.65/kVAh (132 kV and above), ₹7.15 (33 kV) and ₹7.65 (11 kV), with ₹500/kVA. Effective ≈ ₹7.51. FY27 adds a grid support charge of ₹19.77/kW/month and a green tariff of +₹0.66/kWh.
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City | EHV node [E] | Water | Hazard | DB/WB; FC h [E] | Demand | Scores | Total | Tier
1 | Hyderabad periphery – Chandanvelly/Meerkhanpet/Shadnagar (17.10, 78.20; Rangareddy) | 400 kV Shankarpally / 765 kV Maheshwaram, 10–25 km | Mixed; Krishna/Godavari municipal supply [E] | II | 40.5/25.5; ~900 | 151 MW op / 710 MW upcoming [R] | 6.7/7/10/6/5/9/7/6/9 | 7.2 | A
2 | Hyderabad core – Gachibowli/Nanakramguda (17.44, 78.35; Rangareddy) | 400 kV Shankarpally, ~15 km | Urban over-draft pockets [E] | II | 40.5/25.5; ~900 | as above | 6.5/7/10/4/5/9/3/6/10 | 6.7 | A
3 | Warangal (17.97, 79.59; Hanamkonda) | 400 kV Warangal, ~10 km | Safe [E] | II | 42/26; ~800 | Low | 5.65/4/9.5/7/5/9/9/6/3 | 6.4 | A
R10-T10 State shortlist: Andhra Pradesh
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Andhra Pradesh
Note: Tariff: FY2026-27 APERC tariffs are unchanged from FY26 [R]. HT-I demand charge is about ₹475/kVA [R, older order]; the energy charge is not confirmed. Effective ≈ ₹7.3 [E].
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City | EHV node [E] | Water | Hazard | DB/WB; FC h [E] | Demand | Scores | Total | Tier
1 | Visakhapatnam – Tarluvada/Adavivaram/Rambilli (17.69, 83.22; Visakhapatnam/Anakapalli) | 400 kV Kalpaka, 10–25 km; new dedicated EHV planned | Safe [E] | II; very high cyclone | 37/29; ~100 | Google 1 GW (601 acres) [R]; 5 GW promised [R] | 6.55/8/7.9/7/1/4/9/9/6 | 6.8 | A
2 | Sri City / Tirupati (13.53, 79.99; Tirupati) | 220 kV in park; 400 kV unverified | Mixed [E] | III; moderate cyclone | 39/28; ~0 | 55 km from Chennai cable landings | 6.05/7/9.8/5/1/6/8/9/4 | 6.4 | A
3 | Anantapur (14.68, 77.60; Anantapur) | 400 kV RE pooling (Uravakonda/Hindupur), 20–40 km | Drought-prone; over-exploited blocks [E] → conditional | II | 40/25; ~600 | Nil; RE-rich | 7.05/3/10/3/4/9/10/9/2 | 6.3 | A (conditional)
4 | Amaravati / Vijayawada (16.51, 80.52; Guntur/NTR) | 400 kV Vijayawada area, ~20 km | Safe [E] | III; Krishna floods | 41/28; ~150 | Capital build-out | 6.05/4/9.6/7/2/6/7/9/3 | 6.2 | B
R10-T11 State shortlist: Uttar Pradesh
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Uttar Pradesh
Note: Land [R]: YEIDA's 2026 residential allotment rate is ₹36,260/m². Industrial/DC rates are lower [U].
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City | EHV node [E] | Water | Hazard | DB/WB; FC h [E] | Demand | Scores | Total | Tier
1 | Greater Noida – NIDP/Knowledge Park (28.47, 77.50; Gautam Buddh Nagar) | 765/400 kV Greater Noida, 5–15 km | Semi-critical to over-exploited [E]; Ganga canal + STP | IV | 43.5/29; ~2,800 | NCR 183 MW op / 387 MW upcoming [R] | 6.35/8/6.1/4/4/6/7/9/8 | 6.4 | A
2 | Noida – Sec 62/132/143 (28.54, 77.39; Gautam Buddh Nagar) | 400 kV Noida, 5–10 km | Over-exploited [E] → conditional | IV | 43.5/29; ~2,800 | NIXI Delhi node in Noida | 5.35/9/6.1/3/4/6/4/9/9 | 6.1 | B
3 | YEIDA / Jewar (28.17, 77.60; Gautam Buddh Nagar) | 400 kV Jahangirpur ~15 km | Semi-critical [E] | IV | 43.5/29; ~2,800 | Airport-led | 5.35/6/6.2/5/4/6/9/9/5 | 6 | B
4 | Lucknow (26.85, 80.95; Lucknow) | 765 kV Unnao / 400 kV Lucknow, 20–40 km | Urban over-exploited [E] | III | 43/29.5; ~2,500 | NIXI node | 4.85/5/6.0/3/4/7/8/9/5 | 5.5 | B
5 | Kanpur (26.45, 80.33; Kanpur Nagar) | 400 kV Panki ~10 km | Semi-critical [E] | III | 44/29.5; ~2,400 | Low | 4.85/3/6.0/4/4/7/8/9/3 | 5.2 | C
R10-T12 State shortlist: Haryana
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Haryana
Note: Tariff [R]: HERC kept FY27 tariffs equal to FY26. HT is ₹290/kVA plus ₹6.95/kVAh at 11 kV, ₹6.85 at 33 kV, and about ₹6.6 at 66–132 kV (OCR uncertain). Effective ≈ ₹7.1.
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City | EHV node [E] | Water | Hazard | DB/WB; FC h [E] | Demand | Scores | Total | Tier
1 | Gurugram – Manesar/Sohna (28.46, 77.03; Gurugram) | PGCIL 400 kV Gurugram / Daultabad, 5–15 km | State 136.75%; 5 over-exploited blocks [R] → conditional | IV | 44/28.5; ~2,800 | NCR enterprise/cloud | 6.4/8/6.1/1/4/6/3/5/9 | 5.5 | B (conditional)
2 | Sonipat – Kundli/Kharkhoda (28.99, 77.02; Sonipat) | 400 kV Deepalpur ~15 km | Over-exploited [R, district list] → conditional | IV | 44/29; ~3,000 | Low | 6.4/5/6.1/1/4/6/7/5/5 | 5 | C
R10-T13 State shortlist: Delhi
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Delhi
Note: Tariff: DERC figures not retrieved [U]; effective ≈ ₹8.5 [E].
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City | EHV node [E] | Water | Hazard | DB/WB; FC h [E] | Demand | Scores | Total | Tier
1 | Delhi – Okhla/Narela/Bawana (28.61, 77.21; various) | 400 kV Bawana / Mundka / Tughlakabad, 5–15 km | Largely over-exploited [E] | IV; Yamuna floodplain | 43.5/29; ~2,800 | Core NIXI; edge demand | 3.35/10/6.1/1/4/6/1/3/10 | 4.7 | C (edge only)
R10-T14 State shortlist: Gujarat
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Gujarat
Note: Tariff: GERC FY27 tariffs are unchanged. The HTP-I energy charge is ₹4.30/unit plus FPPPA (base about ₹2.15), and the demand-charge slabs were not verified. The all-in figure is ₹7.5–8.5 (secondary source), so ≈ ₹8.0 is used. Open-access additional surcharge is ₹0.99/kWh for October 2026 – March 2027 [R].
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City | EHV node [E] | Water | Hazard | DB/WB; FC h [E] | Demand | Scores | Total | Tier
1 | GIFT City / Gandhinagar (23.16, 72.68; Gandhinagar) | 220 kV in city; 400 kV Dehgam ~25 km | Narmada supply; semi-critical [E] | III | 43/28; ~900 | IFSC, BFSI DR | 5.3/6/8.0/5/3/7/6/8/6 | 6 | B
2 | Ahmedabad (23.02, 72.57; Ahmedabad) | 400 kV Dehgam / Vadavi, 15–25 km | Critical [E] | III | 43/28; ~900 | NIXI Ahmedabad | 5.3/6/8.0/4/3/7/6/8/7 | 5.9 | B
3 | Jamnagar (22.47, 70.06; Jamnagar) | 400 kV Hadala/Jamnagar ~20 km | Desal | IV [E]; cyclone | 40/28; ~600 | Reliance AI campus [R, announced] | 5.8/4/6.9/4/3/5/8/8/3 | 5.3 | B
4 | Dholera SIR (22.25, 72.19; Ahmedabad) | New 400 kV in SIR [E] | Saline; canal water | III; low-lying | 42/28; ~800 | Greenfield | 5.3/3/8.2/4/3/5/9/8/2 | 5.2 | C
R10-T15 State shortlist: West Bengal
Source: Report 10 (Part 10 research report) · State-by-state shortlists › West Bengal
Note: Tariff: WBERC FY26 sets a ₹320/kVA demand charge [R]; the energy charge is unverified, and ≈ ₹7.5 effective is used [E].
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City | EHV node [E] | Water | Hazard | DB/WB; FC h [E] | Demand | Scores | Total | Tier
1 | Kharagpur (22.35, 87.32; Paschim Medinipur) | 400 kV Kharagpur ~10 km | Safe to semi-critical [E] | III; cyclone moderate | 40/29.5; ~800 | Backhaul for Digha CLS | 4.7/6/4.3/6/2/5/8/4/1 | 4.9 | C
2 | Kolkata – New Town / Bengal Silicon Valley (22.57, 88.36; North 24 Parganas) | 400 kV Subhasgram ~25 km | Hooghly supply; mixed [E] | III; flood; cyclone (Amphan) | 37.5/29.5; ~1,000 | 22 MW op / 84 MW upcoming [R] | 5.2/6/3.5/5/2/4/6/4/5 | 4.8 | C
3 | Digha (21.63, 87.51; Purba Medinipur) | Nearest 400 kV ~90 km → fails 25 km filter | Safe [E] | Very high cyclone | 36/29.5; ~300 | Jio CLS (pending) | 4.7/6/4.3/6/2/2/8/4/1 | 4.6 | C (CLS only)
R10-T16 State shortlist: Kerala
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Kerala
Note: Tariff [R]: KSERC Order of 5 December 2024, valid to 31 March 2027, sets energy charges of ₹6.75 (HT-I), ₹6.15 (110 kV) and ₹5.55 (220 kV). Demand charges are about ₹390–400/kVA [E]. Effective ≈ ₹6.23 at 220 kV.
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City | EHV node [E] | Water | Hazard | DB/WB; FC h [E] | Demand | Scores | Total | Tier
1 | Kochi – Kakkanad/Infopark (9.93, 76.27; Ernakulam) | 400 kV Kochi East ~10 km | Safe; ~3,000 mm rainfall | III; 2018 floods | 33.5/27.5; 0 | Cable landings (Tata, others) + NIXI | 7.5/8/7.5/7/1/5/4/4/6 | 6.3 | A
2 | Thiruvananthapuram – Technopark (8.52, 76.94; Thiruvananthapuram) | 400 kV Pothencode ~15 km | Safe | III | 33/27; 0 | CLS + NIXI | 7.0/7/6.5/7/1/6/4/4/5 | 6 | B
R10-T17 State shortlist: Odisha
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Odisha
Note: Tariff [R]: OERC RST order of 24 March 2026 (FY27) sets EHT large industry at ₹250/kVA, with 580 paise/kVAh up to 60% load factor and 470 paise above. It also gives a 30 p rebate above 80% load factor and a 10% discount during solar hours from July 2026. Effective ≈ ₹5.96, the lowest found.
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City | EHV node [E] | Water | Hazard | DB/WB; FC h [E] | Demand | Scores | Total | Tier
1 | Jharsuguda (21.86, 84.01; Jharsuguda) | 765/400 kV Jharsuguda (PGCIL) ~10 km | Hirakud; safe [E] | II–III; inland | 45/27; ~1,000 | Nil; power-intensive industry hub | 9.0/2/6.5/7/3/8/9/6/1 | 6.3 | A
2 | Bhubaneswar – Infovalley (20.30, 85.82; Khordha) | 400 kV Mendhasal ~15 km | Safe [E] | III; very high cyclone (Fani) | 41/29; ~400 | NIXI Bhubaneswar/Cuttack; planned CLS | 8.5/5/5.8/7/2/4/8/6/4 | 6.2 | B
R10-T18 State shortlist: Rajasthan
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Rajasthan
Note: Tariff: about ₹380/kVA + ₹6.50/kWh (aggregator, unconfirmed); effective ≈ ₹7.7 [E].
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City | EHV node [E] | Water | Hazard | DB/WB; FC h [E] | Demand | Scores | Total | Tier
1 | Jaipur – Mahindra World City/Sitapura (26.91, 75.79; Jaipur) | 400 kV Heerapura, 10–20 km | Over-exploited [E] → conditional | II | 43/27.5; ~2,300 | Moderate | 5.8/4/6.9/1/4/9/8/7/5 | 5.3 | B (conditional)
2 | Jodhpur (26.24, 73.02; Jodhpur) | 400 kV Surpura ~10 km | Over-exploited [E] → conditional | II; heat | 44/26; ~1,700 | Bhadla solar | 6.3/2/6.3/1/3/9/9/7/2 | 5 | C
R10-T19 State shortlist: Madhya Pradesh
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Madhya Pradesh
Note: Tariff: MPERC FY27 HV-3 at 132 kV is ₹729/kVA, with 734/635 paise split by load factor (snippets; column mapping uncertain). Effective ≈ ₹8.2.
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
Rank | City | EHV node [E] | Water | Hazard | DB/WB; FC h [E] | Demand | Scores | Total | Tier
1 | Bhopal (23.26, 77.41; Bhopal) | 400 kV Bhopal ~15 km | Semi-critical [E] | II | 41.5/26; ~1,800 | NIXI node | 4.4/4/8.5/5/5/9/8/6/4 | 5.7 | B
2 | Indore – Super Corridor/Pithampur (22.72, 75.86; Indore/Dhar) | 400 kV Indore / Pithampur ~15 km | Over-exploited [E] → conditional | III | 41/26; ~1,800 | NIXI node | 4.4/5/8.8/2/5/7/8/6/5 | 5.2 | C
R10-T20 Secondary states shortlist
Source: Report 10 (Part 10 research report) · State-by-state shortlists › Secondary states
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 10 map dots, detail panel and ranking table (site attributes and scores).
Used to derive: Filter pass/fail, factor scores and tier for each city in the state.
State | City (lat, long; district) | Key raw facts | Scores | Total | Tier
Chhattisgarh | Nava Raipur (21.16, 81.79; Raipur) | Surplus coal-based state grid; 400 kV Raita ~25 km [E]; zone II; NIXI Raipur | 7.45/4/8.0/7/4/9/9/4/2 | 6.4 | A
Jharkhand | Ranchi (23.34, 85.31; Ranchi) | 400 kV Ranchi ~15 km [E]; zone II; mild plateau climate | 5.75/4/5.3/5/6/9/8/3/2 | 5.3 | B
Goa | Verna (15.36, 73.93; South Goa) | NIXI Panjim; ~430 km from Mumbai cable landings; zone III | 5.1/4/9.4/7/2/6/4/4/2 | 5.3 | B
Uttarakhand | Dehradun (30.32, 78.03; Dehradun) | Zone IV (Zone VI in the withdrawn 2025 draft); cool climate; hydro | 6.5/3/4.5/7/8/4/4/4/3 | 5.1 | C
Himachal Pradesh | Baddi–Nalagarh (30.95, 76.79; Solan) | Low hydro tariff [E]; 400 kV Nalagarh ~10 km; zone IV | 8.0/2/4.2/5/7/4/6/3/1 | 4.9 | C
Punjab | Mohali (30.70, 76.72; SAS Nagar) | PSERC FY26 industrial ₹5.82–7.04/kVAh [R]; over-exploited [E]; zone IV; NIXI Chandigarh | 6.1/5/4.2/2/5/6/6/4/5 | 4.8 | C
Bihar | Patna (25.59, 85.14; Patna) | Zone IV; Ganga floods; NIXI node | 3.8/4/4.5/6/3/3/7/4/2 | 4.2 | C
Assam / NE | Guwahati (26.14, 91.74; Kamrup Metro) | Zone V; Brahmaputra floods; NIXI core node | 4.7/4/0/7/4/1/7/4/2 | 4 | Excluded (zone V) – regional edge only, with seismic isolation
R10-T21 National master table (default weights)
Source: Report 10 (Part 10 research report) · National master table (default weights)
Data basis: Calculated (model output)
Used in atlas: Ch 10 ranking table; worked-example workbook.
Used to derive: National rank and tier.
# | City | State | District | Lat | Long | Score | Tier | Key strength | Key weakness
1 | Hyderabad periphery | Telangana | Rangareddy | 17.1 | 78.2 | 7.2 | A | Grid + ₹6.65/kVAh + zone II | No cable landing (Vizag/Chennai backhaul)
2 | Visakhapatnam | AP | Visakhapatnam/Anakapalli | 17.69 | 83.22 | 6.8 | A | Gigawatt anchor + new cable landings + policy | Cyclone
3 | Hyderabad core | Telangana | Rangareddy | 17.44 | 78.35 | 6.7 | A | Ecosystem, talent | Land cost, water
4 | Navi Mumbai | Maharashtra | Thane/Raigad | 19.03 | 73.03 | 6.6 | A | Cables, interconnection | Tariff ≈ ₹8.7, land
5 | Mysuru | Karnataka | Mysuru | 12.3 | 76.64 | 6.5 | A | Climate, water, policy | Thin ecosystem
6 | Greater Noida (NIDP) | UP | Gautam Buddh Nagar | 28.47 | 77.5 | 6.4 | A | DC tariff ₹6.95, 765 kV | Zone IV, heat
7 | Hoskote | Karnataka | Bengaluru Rural | 13.07 | 77.8 | 6.4 | A* | Bengaluru latency, cooler climate | Over-exploited water
8 | Sri City | AP | Tirupati | 13.53 | 79.99 | 6.4 | A | Near Chennai cable landings, AP policy | Humid, water
9 | Nava Raipur | Chhattisgarh | Raipur | 21.16 | 81.79 | 6.4 | A | Cheap surplus power, zone II | Coal grid, no ecosystem
10 | Warangal | Telangana | Hanamkonda | 17.97 | 79.59 | 6.4 | A | Land, grid | Talent
11 | Pune | Maharashtra | Pune | 18.52 | 73.86 | 6.3 | A | 120 km to Mumbai, land | Tariff
12 | Nagpur | Maharashtra | Nagpur | 21.15 | 79.09 | 6.3 | A | Geographic centre, zone II | Tariff, heat
13 | Kochi | Kerala | Ernakulam | 9.93 | 76.27 | 6.3 | A | Cable landings + cheap EHT | Policy, land
14 | Anantapur | AP | Anantapur | 14.68 | 77.6 | 6.3 | A* | RE pooling, land | Water, connectivity
15 | Jharsuguda | Odisha | Jharsuguda | 21.86 | 84.01 | 6.3 | A | Cheapest tariff, 765 kV | Connectivity, talent
16 | Bhubaneswar | Odisha | Khordha | 20.3 | 85.82 | 6.2 | B | Tariff | Cyclone
17 | Amaravati | AP | Guntur/NTR | 16.51 | 80.52 | 6.2 | B | Policy, land | Connectivity
18 | Bengaluru core | Karnataka | Bengaluru Urban | 12.97 | 77.59 | 6.1 | B* | Demand, talent | Water (395% East)
19 | Mangaluru | Karnataka | Dakshina Kannada | 12.91 | 74.86 | 6.1 | B | Water, coast | EHV distance
20 | Noida | UP | Gautam Buddh Nagar | 28.54 | 77.39 | 6.1 | B | NIXI, demand | Water, land
21 | GIFT City | Gujarat | Gandhinagar | 23.16 | 72.68 | 6 | B | IFSC, RE | Heat
22 | YEIDA/Jewar | UP | Gautam Buddh Nagar | 28.17 | 77.6 | 6 | B | Land | Ecosystem
23 | Thiruvananthapuram | Kerala | Thiruvananthapuram | 8.52 | 76.94 | 6 | B | Cable landing, tariff | Latency to north
24 | Ahmedabad | Gujarat | Ahmedabad | 23.02 | 72.57 | 5.9 | B | NIXI, policy | Water
25 | Nashik | Maharashtra | Nashik | 20 | 73.79 | 5.8 | B | Near Mumbai, safe water | Tariff
26 | Hosur | Tamil Nadu | Krishnagiri | 12.74 | 77.83 | 5.7 | B | Bengaluru spill-over | TN policy lapsed
27 | Bhopal | MP | Bhopal | 23.26 | 77.41 | 5.7 | B | Zone II, land | Tariff ≈ ₹8.2
28 | Chennai | Tamil Nadu | Chennai and neighbours | 13.08 | 80.27 | 5.5 | B* | 8 cables, 214 MW | Water, flood, policy lapse
29 | Gurugram | Haryana | Gurugram | 28.46 | 77.03 | 5.5 | B* | Demand | Water (136.75% state)
30 | Lucknow | UP | Lucknow | 26.85 | 80.95 | 5.5 | B | Policy | Water, connectivity
31 | Coimbatore | Tamil Nadu | Coimbatore | 11.02 | 76.96 | 5.4 | B | Wind RE | Policy
32 | Jamnagar | Gujarat | Jamnagar | 22.47 | 70.06 | 5.3 | B | Captive RE | Connectivity
33 | Jaipur | Rajasthan | Jaipur | 26.91 | 75.79 | 5.3 | B* | Zone II, RE | Water
34 | Ranchi | Jharkhand | Ranchi | 23.34 | 85.31 | 5.3 | B | Climate, zone II | Policy
35 | Goa (Verna) | Goa | South Goa | 15.36 | 73.93 | 5.3 | B | Latency, water | Scale
36 | Thoothukudi | Tamil Nadu | Thoothukudi | 8.76 | 78.13 | 5.2 | C | Cable landing + RE | Latency, talent
37 | Dholera | Gujarat | Ahmedabad | 22.25 | 72.19 | 5.2 | C | Land | Connectivity
38 | Indore | MP | Indore | 22.72 | 75.86 | 5.2 | C* | Latency | Water, tariff
39 | Kanpur | UP | Kanpur Nagar | 26.45 | 80.33 | 5.2 | C | Policy | Connectivity
40 | Dehradun | Uttarakhand | Dehradun | 30.32 | 78.03 | 5.1 | C | Free cooling | Seismic
41 | Sonipat | Haryana | Sonipat | 28.99 | 77.02 | 5 | C* | Grid | Water
42 | Jodhpur | Rajasthan | Jodhpur | 26.24 | 73.02 | 5 | C* | Solar | Water, connectivity
43 | Kharagpur | West Bengal | Paschim Medinipur | 22.35 | 87.32 | 4.9 | C | Digha backhaul | Policy, demand
44 | Baddi | HP | Solan | 30.95 | 76.79 | 4.9 | C | Hydro tariff | Seismic, connectivity
45 | Kolkata | West Bengal | North 24 Parganas | 22.57 | 88.36 | 4.8 | C | Eastern demand | Hazard, latency, policy
46 | Mohali | Punjab | SAS Nagar | 30.7 | 76.72 | 4.8 | C* | Tariff | Water, latency
47 | Delhi | Delhi | various | 28.61 | 77.21 | 4.7 | C | Interconnection | Water, land, tariff
48 | Digha | West Bengal | Purba Medinipur | 21.63 | 87.51 | 4.6 | C | Cable landing | Cyclone, no EHV within 25 km
49 | Patna | Bihar | Patna | 25.59 | 85.14 | 4.2 | C | — | Flood, zone IV
— | Guwahati | Assam | Kamrup Metro | 26.14 | 91.74 | 4 | Excluded | NE edge | Zone V
R10-T22 Alternate weightings and rank stability
Source: Report 10 (Part 10 research report) · Alternate weightings and rank stability
Data basis: Calculated (model output)
Used in atlas: Ch 10 "Top picks by use case"; Monte Carlo context.
Used to derive: Rank stability across weightings.
City | Default | AI campus | Interconnect | Sustainability | Geo-mean
Hyderabad periphery | 7.2 | 7 | 7.9 | 6.6 | 7
Visakhapatnam | 6.8 | 6.6 | 7.1 | 6.2 | 6.3
Hyderabad core | 6.7 | 6.2 | 7.8 | 5.9 | 6.3
Navi Mumbai | 6.6 | 5.5 | 8.2 | 6.1 | 6
Mysuru | 6.5 | 6.4 | 6 | 7.2 | 6.1
Greater Noida | 6.4 | 6.2 | 7 | 5.3 | 6.2
Hoskote | 6.4 | 6 | 7.2 | 6 | 5.8
Sri City | 6.4 | 6.2 | 6.9 | 5.5 | —
Nava Raipur | 6.4 | 7 | 5.8 | 5.6 | 5.9
Pune | 6.3 | 5.6 | 7.2 | 6.3 | 6.1
Nagpur | 6.3 | 6 | 6.2 | 6.5 | —
Kochi | 6.3 | 6.2 | 6.9 | 5.6 | —
Anantapur | 6.3 | 6.7 | 5.9 | 6.1 | —
Jharsuguda | 6.3 | 7.4 | 5 | 5.2 | —
Bhubaneswar | 6.2 | 6.8 | 5.7 | 5.2 | —
Bengaluru core | 6.1 | 5.4 | 7.5 | 5.6 | 5
Noida | 6.1 | 5.4 | 7.2 | 5 | —
GIFT City | 6 | 5.8 | 6.4 | 6.2 | —
Chennai | 5.5 | 4.6 | 7.6 | 4.7 | 4.7
Gurugram | 5.5 | 5.1 | 6.7 | 4.1 | 4.6
Jamnagar | 5.3 | 5.6 | 5.1 | 5.6 | —
Kolkata | 4.8 | 4.8 | 4.9 | 4 | —
Delhi | 4.7 | 3.7 | 6.8 | 4 | 3.7

## R11
Report 11 · Forecast to 2035
28 tables. Source line under each title; "Note" gives the context sentence from the report.
R11-T01 Historical capacity series
Source: Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.1 Historical series
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 11 history points on the capacity chart.
Used to derive: Fitted CAGR (27.9%) and logistic rate.
Year-end | Harmonised base series used for fitting (MW IT) | Reported points (source) | Label
2019 | 375 | 350 (JLL); about 400 (C&W) | E from R
2020 | 450 | 375 (MeitY, Parliament reply, Mar 2026); 520 (JM Financial via CEEW, broader definition) | E from R
2021 | 560 | 499 at H1 2021 (JLL); 824 at end-2021 (C&W, colocation stock, inconsistent with C&W's later series) | E from R
2022 | 720 | 722 (JLL) | R
2023 | 977 | 977 at H2 2023 (C&W; 258 MW built in 2023, +105% YoY); 950 in FY24 (ICRA) | R
2024 | 1200 | 1,030 (JLL); about 1,150 in Dec 2024 (ICRA); 1,255 (CBRE) | E from R
H1 2025 | – | 1,280 (C&W); 1,263 in Apr 2025 (Colliers); 1,123 (JLL) | R
2025 | 1611 | 1,789 − 178 (C&W, derived); about 1,500 (MeitY); about 1.7 GW (CBRE); 387 MW added in 2025 (Rubix) | E from R
H1 2026 | 1789 | C&W: 1,789 across 7 markets, 147 facilities, 33 providers, 14.9% vacancy; JLL: 1,637 MW (2026 Mid-Year Report, June 2026); PIB factsheet (14 Sep 2026): 1.57 GW as of Aug 2026 | R
2026E | 2000 | CBRE: about 2 GW by end-2026; C&W: Mumbai to exceed 1 GW by end-2026 | E
R11-T02 CAGR model: forward scenarios from 1,611 MW
Source: Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.2 Model (a): CAGR, C(t) = C₀(1+g)^t
Note: Forward scenarios from C₀ = 1,611 MW (end-2025) [M]:
Data basis: Calculated (model output)
Used in atlas: Ch 11 CAGR model option.
Used to derive: Capacity path under constant growth.
g | 2027 | 2028 | 2030 | 2033 | 2035
Low 18% | 2243 | 2647 | 3686 | 6055 | 8431
Base 25% | 2517 | 3146 | 4916 | 9602 | 15003
High 32% | 2807 | 3705 | 6456 | 14849 | 25872
R11-T03 Logistic model parameters
Source: Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.3 Model (b): logistic S-curve, C(t) = K / (1 + e^(−r(t − t₀)))
Note: t₀ = 2025 + ln(K/1,611 − 1) / r
Data basis: Proxy / estimate
Used in atlas: Ch 11 S-curve sliders (K, r).
Used to derive: Logistic midpoint t₀.
Parameter | Low | Base | High
K (MW) | 12000 | 25000 | 45000
r (/yr) | 0.24 | 0.26 | 0.3
t₀ | 2032.8 | 2035.3 | 2036
R11-T04 Logistic model output (MW)
Source: Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.3 Model (b): logistic S-curve, C(t) = K / (1 + e^(−r(t − t₀)))
Note: Logistic output (MW) [M]:
Data basis: Calculated (model output)
Used in atlas: Ch 11 S-curve model option.
Used to derive: Capacity path to 2035.
Year | Low | Base | High
2026 | 1975 | 2051 | 2146
2027 | 2403 | 2596 | 2850
2028 | 2897 | 3266 | 3763
2029 | 3457 | 4077 | 4936
2030 | 4076 | 5044 | 6417
2031 | 4745 | 6171 | 8249
2032 | 5447 | 7458 | 10465
2033 | 6166 | 8884 | 13062
2034 | 6879 | 10425 | 16008
2035 | 7568 | 12030 | 19215
R11-T05 Forecast conversion evidence (backtest)
Source: Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.4 Model (c): pipeline conversion, C(t+1) = C(t) + Σ P_stage(t − L) × c_stage
Note: Conversion evidence:
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 11 haircut KPI (0.58–0.87×).
Used to derive: Delivery haircut on forecasts.
Source and date | Forecast | Outcome | Ratio | Label
JLL H1 2021 update | 499 → 1,008 MW by 2023 (+509) | JLL's 2023 figure was not published in our sources. Interpolated between 722 (2022) and 1,030 (2024) it is about 875; C&W reports 977 | Additions about 0.74; level about 0.87 | E
JLL (about 2023) | +681 MW to 1,318 MW by end-2024 | 1,030 MW (JLL 2024) | Additions 0.58; level 0.78 | R/M
C&W, Feb 2022 | "over 1.0 GW incremental … in various stages of construction, expected to start operations over the next 4–5 years" | About 1,070 MW added from end-2022 to H1 2026 | About 1.0 within 4.5 years | R/M
ICRA, Oct 2024 | 950 MW (FY24) → 2,000–2,100 MW by Mar 2027 | On track on C&W's basis (1,789 at H1 2026); marginal on JLL's basis (1,637 MW at June 2026) | About 0.9–1.0 (provisional) | M
Arizton / ResearchAndMarkets | 3.5 GW by 2030 (Feb 2025), revised to 4.8 GW (Jul 2025) | Forecast inflated by 37% in 5 months | n/a | R
CEEW / Systemiq | "Only about 50% of the USD ~95 bn worth of capital committed … between 2019 and 2025 has a …" (text truncated in source) | Treated as a conversion ceiling for announcements of about 50% | about 0.5 | R (partial)
R11-T06 Pipeline conversion parameters
Source: Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.4 Model (c): pipeline conversion, C(t+1) = C(t) + Σ P_stage(t − L) × c_stage
Note: Parameters [E]:
Data basis: Proxy / estimate
Used in atlas: Ch 11 pipeline-conversion sliders.
Used to derive: Expected delivered MW from pipeline.
Stage | Conversion c | Lag L
Under construction | Low 0.85 / Base 0.95 / High 1.0 | 1–2 years
Planned | Low 0.40 / Base 0.60 / High 0.80 | 2–4 years (base 3)
MoU / announced only | 0.2–0.5 | 3–5 years
R11-T07 Pipeline-conversion path to 2030 (MW)
Source: Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.4 Model (c): pipeline conversion, C(t+1) = C(t) + Σ P_stage(t − L) × c_stage
Note: High: 1,789 + 509 + 2,681 = 4,979 MW, plus about 1,000 MW of gigawatt-campus phases outside C&W's 7 markets (Visakhapatnam, Jamnagar) [E] = about 6,000 MW.
Data basis: Calculated (model output)
Used in atlas: Ch 11 pipeline model option.
Used to derive: Capacity to 2030.
Path (MW) | 2026 | 2027 | 2028 | 2029 | 2030
Low | 1950 | 2250 | 2650 | 3100 | 3560
Base | 1990 | 2450 | 3050 | 3650 | 4280
High | 2050 | 2800 | 3800 | 4900 | 6000
R11-T08 Integrated capacity path 2026–2035 (MW IT)
Source: Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.5 Integrated capacity path
Note: 2031–2035: the logistic model, with the base case trimmed by about 10% to stay consistent with the conversion haircut.
Data basis: Calculated (model output)
Used in atlas: Ch 11 integrated base case (default chart).
Used to derive: Base / low / high capacity path.
MW IT | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Low | 1950 | 2250 | 2650 | 3100 | 3600 | 4200 | 4800 | 5450 | 6100 | 6800
Base | 2000 | 2500 | 3100 | 3850 | 4700 | 5700 | 6850 | 8100 | 9450 | 10800
High | 2100 | 2850 | 3800 | 4950 | 6400 | 8200 | 10300 | 12800 | 15600 | 18800
R11-T09 Published forecasts compared
Source: Report 11 (Part 11 research report) · 1. Capacity (MW IT): data, three models, comparison, backtest › 1.6 Published forecasts compared
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 11 "Published forecasts compared" chart.
Used to derive: Our base vs consultant median.
Forecaster | 2026–27 | 2028–29 | 2030 | 2031–35 | Label
ICRA | 2,000–2,100 MW by Mar 2027; edge capacity 200–210 MW by 2027 | – | – | 3.0–3.5 GW pipeline over 7–10 years, ₹2.0–2.3 lakh crore | R
JLL | about 2.1 GW (2027); earlier 1,825 MW (2027) | 6 GW (2029) | – | – | R
CBRE | about 2 GW (end-2026); about 500 MW of supply in 2026 | – | – | – | R
C&W | – | – | 1,789 + 3,860 pipeline = about 5.6 GW if fully delivered; US$29.9 bn | – | R
Colliers | – | – | more than 4,500 MW (top 7 cities) | – | R
CareEdge | – | – | about 4 GW (FY30), about ₹1.5 lakh crore | – | R
Arizton (via ResearchAndMarkets) | – | – | 4.8 GW | – | R
Rubix | – | – | 6.5 GW | – | R
Macquarie | 2× by 2027 | – | 5× by 2030 (about 6.5–7.5 GW implied) | – | R/E
Jefferies | – | – | 8 GW; US$30 bn capex | – | R
PIB factsheet (14 Sep 2026) | – | – | "nearly 8 GW"; US$70 bn ongoing plus US$90 bn announced | – | R
Wood Mackenzie | – | – | 12 GW (from 2.2 GW in 2025); AI capacity 275 → 6,546 MW | – | R
CEA / Ministry of Power (demand, GW of power) | – | – | – | 17 GW (CEA) / 13.56 GW (MoP, Mar 2026) by 2031-32; 26.3 GW additional AI data-centre load (MoS Power, Jul 2026) | R
This report (base) | 2.0 / 2.5 GW | 3.1 / 3.85 GW | 4.7 GW | 6.85 GW (2032); 10.8 GW (2035) | M
R11-T10 Electricity, base case: MW, utilisation, PUE, TWh and share
Source: Report 11 (Part 11 research report) · 2. Electricity (TWh) and share of the grid
Note: Base case [M] (calendar-year data-centre energy against the matching fiscal year's requirement; year-end MW basis, so use the mid-year average to get figures about 8–10% lower):
Data basis: Calculated (model output)
Used in atlas: Ch 11 electricity and share outputs.
Used to derive: TWh and % of national demand.
Year | MW | u | PUE | IT TWh | Facility TWh | India requirement (BU) | Data-centre share
2026 | 2000 | 0.55 | 1.5 | 9.6 | 14.5 | 1918 | 0.75%
2027 | 2500 | 0.56 | 1.48 | 12.3 | 18.2 | 2041 | 0.89%
2028 | 3100 | 0.57 | 1.46 | 15.5 | 22.6 | 2172 | 1.04%
2029 | 3850 | 0.58 | 1.44 | 19.6 | 28.2 | 2311 | 1.22%
2030 | 4700 | 0.6 | 1.42 | 24.7 | 35.1 | 2459 | 1.43%
2031 | 5700 | 0.61 | 1.41 | 30.5 | 43 | 2617 | 1.64%
2032 | 6850 | 0.62 | 1.4 | 37.2 | 52.1 | 2785 | 1.87%
2033 | 8100 | 0.63 | 1.38 | 44.7 | 61.7 | 2963 | 2.08%
2034 | 9450 | 0.64 | 1.37 | 53 | 72.6 | 3153 | 2.30%
2035 | 10800 | 0.65 | 1.35 | 61.5 | 83 | 3355 | 2.47%
R11-T11 Electricity scenarios
Source: Report 11 (Part 11 research report) · 2. Electricity (TWh) and share of the grid
Note: Scenarios [M]:
Data basis: Calculated (model output)
Used in atlas: Ch 11 scenario comparison.
Used to derive: Low/base/high electricity.
Scenario | 2030 TWh | 2030 share | 2035 TWh | 2035 share | Year share reaches 1% / 2% / 3%
Low (u 0.50→0.58; PUE 1.52→1.42) | 24.7 | 1.0% | 49.1 | 1.5% | 2030 / not reached / not reached
Base | 35.1 | 1.4% | 83 | 2.5% | 2028 / 2033 / after 2035
High (u 0.60→0.72; PUE 1.50→1.30) | 51 | 2.1% | 154.2 | 4.6% | 2027 / 2030 / about 2032
R11-T12 State-level electricity shares, base case
Source: Report 11 (Part 11 research report) · 2. Electricity (TWh) and share of the grid
Note: State-level shares, base case [M; state denominators are E]. These are approximate state requirements, extrapolated about 6%/yr from FY25. Replace them with the state tables of the 20th EPS mid-term review before publishing.
Data basis: Proxy / estimate
Used in atlas: Ch 11 state share outputs (denominators are estimates).
Used to derive: Grid stress by state.
State (data-centre cities) | 2030 DC TWh | ≈ State BU 2030 [E] | Share | 2035 DC TWh | ≈ State BU 2035 [E] | Share
Maharashtra (Mumbai/Navi Mumbai, Pune) | 17.9 | 250 | 7.2% | 39.9 | 330 | 12.1%
Telangana (Hyderabad) | 4.8 | 120 | 4.0% | 12.2 | 160 | 7.6%
Tamil Nadu (Chennai) | 3.5 | 175 | 2.0% | 11 | 230 | 4.8%
Andhra Pradesh (Visakhapatnam) | 1.9 | 105 | 1.8% | 4.9 | 140 | 3.5%
Karnataka (Bengaluru, Mysuru) | 1.7 | 120 | 1.4% | 3.9 | 160 | 2.4%
Uttar Pradesh (Noida/Greater Noida, about 70% of NCR) | 2.4 | 210 | 1.1% | 5.5 | 280 | 2.0%
R11-T13 Grid emission factor history (CEA)
Source: Report 11 (Part 11 research report) · 3. Carbon trajectory
Note: Grid emission factor history (CEA CO₂ Baseline Database, weighted average including renewables) [R]:
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 11 carbon inputs; all calculators (0.710).
Used to derive: Grid carbon trend.
Fiscal year | EF (tCO₂/MWh)
FY14 | 0.774
FY21 | 0.703 (COVID year)
FY23 | 0.716
FY24 | 0.727
FY25 | 0.710 (v21: 1,234.19 Mt ÷ 1,739.06 BU)
R11-T14 Emission-factor paths
Source: Report 11 (Part 11 research report) · 3. Carbon trajectory
Note: EF paths (tCO₂/MWh) [E]:
Data basis: Proxy / estimate
Used in atlas: Ch 11 EF slider paths.
Used to derive: Future grid carbon.
Year | Slow | Base | Fast
2026 | 0.71 | 0.7 | 0.69
2030 | 0.69 | 0.62 | 0.55
2035 | 0.65 | 0.535 | 0.45
R11-T15 Emissions, base case
Source: Report 11 (Part 11 research report) · 3. Carbon trajectory
Note: Emissions, base case [M]:
Data basis: Calculated (model output)
Used in atlas: Ch 11 carbon outputs.
Used to derive: Net and location-based CO₂.
Year | Facility TWh | EF | Clean share | Net MtCO₂ | Location-based Mt (clean = 0)
2026 | 14.5 | 0.7 | 0.3 | 7.1 | 10.1
2027 | 18.2 | 0.68 | 0.33 | 8.3 | 12.3
2028 | 22.6 | 0.66 | 0.37 | 9.4 | 14.9
2029 | 28.2 | 0.64 | 0.4 | 10.8 | 18
2030 | 35.1 | 0.62 | 0.43 | 12.4 | 21.7
2031 | 43 | 0.6 | 0.47 | 13.7 | 25.8
2032 | 52.1 | 0.58 | 0.5 | 15.1 | 30.2
2033 | 61.7 | 0.565 | 0.53 | 16.4 | 34.9
2034 | 72.6 | 0.55 | 0.57 | 17.2 | 39.9
2035 | 83 | 0.535 | 0.6 | 17.8 | 44.4
R11-T16 Build-cost data points
Source: Report 11 (Part 11 research report) · 4. Costs: build cost per MW and GPU-hour prices › 4.1 Build cost
Note: Data points:
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 11 cost inputs.
Used to derive: Base cost and learning test.
Source | Figure | Implied ₹ crore/MW | Label
Turner & Townsend 2025 index | Mumbai US$6.64/W (₹589/W per IBEF); 51st of 52 markets. Tokyo US$15.2, Singapore US$14.5. Global +5.5% in 2025, +9.0% in 2024 | about 58.4 | R
ICRA (Oct 2024) | ₹50,000–55,000 crore for about 1,100 MW (FY25–27) | about 47 | R/M
ICRA (Mar 2025) | ₹2.0–2.3 lakh crore for a 3.0–3.5 GW pipeline | about 62–70 | R/M
C&W (Sep 2026) | US$29.9 bn for 3,860 MW | about 69 (US$7.75m/MW) | R/M
Jefferies | US$4–5m/MW | 36–45 | R
C&W 2026 APAC guide (via secondary source) | US$5.9–9.0m/MW across India's five major cities | 52–80 | R (secondary)
CareEdge | 4 GW by FY30 needs about ₹1.5 lakh crore; costs up 50–70% recently | about 54 | R/M
US AI vs standard (Quartz, citing industry) | US$20m+/MW vs US$10–12m/MW | AI premium ×1.7–2.0 | R
R11-T17 Build-cost path (₹ crore/MW)
Source: Report 11 (Part 11 research report) · 4. Costs: build cost per MW and GPU-hour prices › 4.1 Build cost
Note: Cost path [M]:
Data basis: Calculated (model output)
Used in atlas: Ch 11 cost outputs.
Used to derive: ₹ crore per MW path.
₹ crore/MW | 2026 | 2027 | 2028 | 2029 | 2030 | 2032 | 2035
Air-cooled facility | 59.4 | 60.4 | 61.5 | 62.6 | 63.8 | 66.5 | 71.5
AI / liquid-cooled facility (×1.5) | 89 | 91 | 92 | 94 | 96 | 100 | 107
Blended new build | 71.3 | 74 | 76.9 | 79.8 | 82.9 | 87.8 | 96.5
R11-T18 Cumulative facility capex, base case
Source: Report 11 (Part 11 research report) · 4. Costs: build cost per MW and GPU-hour prices › 4.1 Build cost
Note: Cumulative facility capex, base case (2026 onward; excludes land and IT/GPU hardware) [M]:
Data basis: Calculated (model output)
Used in atlas: Ch 11 capex outputs.
Used to derive: Cumulative investment.
Year | ΔMW | Annual ₹ crore | Cumulative ₹ lakh crore | Cumulative US$ bn
2026 | 389 | 27700 | 0.28 | 3.1
2027 | 500 | 37000 | 0.65 | 7.3
2028 | 600 | 46100 | 1.11 | 12.5
2029 | 750 | 59900 | 1.71 | 19.2
2030 | 850 | 70500 | 2.42 | 27.2
2031 | 1000 | 85300 | 3.27 | 36.7
2032 | 1150 | 101000 | 4.28 | 48.1
2033 | 1250 | 113000 | 5.41 | 60.8
2034 | 1350 | 126000 | 6.67 | 75
2035 | 1350 | 130300 | 7.97 | 89.6
R11-T19 India H100 commercial rates
Source: Report 11 (Part 11 research report) · 4. Costs: build cost per MW and GPU-hour prices › 4.2 GPU-hour prices
Note: India commercial rates:
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 7 market prices; Ch 11 GPU path start.
Used to derive: GPU price base.
Provider | H100 rate
JarvisLabs | ₹217.89/hr (US$2.69)
Cyfuture | ₹219/hr (SXM)
Neysa | ₹395/hr on demand; about ₹219/hr on a 36-month commitment
Hyperscalers in India (8-GPU instances) | about ₹850–1,050 per GPU-hour
R11-T20 GPU-hour price path (₹)
Source: Report 11 (Part 11 research report) · 4. Costs: build cost per MW and GPU-hour prices › 4.2 GPU-hour prices
Note: We use −20%/yr as the base for an H100-class hour from 2026.
Data basis: Calculated (model output)
Used in atlas: Ch 11 GPU price outputs.
Used to derive: GPU-hour price path.
₹ per GPU-hour (India commercial on-demand) | 2026 | 2027 | 2028 | 2029 | 2030
H100-class, base (−20%/yr) | 220 | 176 | 141 | 113 | 90
H100-class, low decline (−10%/yr) | 220 | 198 | 178 | 160 | 144
H100-class, high decline (−30%/yr) | 220 | 154 | 108 | 75 | 53
Frontier class (B200/GB200 → successors) [E] | about 450–550 | about 450–550 | about 450–550 | about 450–550 | about 450–550
R11-T21 Dry/liquid share, WUE mix and national water
Source: Report 11 (Part 11 research report) · 5. Water demand by city (MLD)
Note: The evaporative share of the non-dry remainder falls from 69% to 50% by 2035 [E].
Data basis: Calculated (model output)
Used in atlas: Ch 11 water outputs (Bass diffusion).
Used to derive: National on-site MLD.
Year | Dry/liquid share | WUE_mix (L/kWh) | National on-site water, base (MLD)
2026 | 22% | 1.09 | 28.7
2027 | 26% | 1.03 | 34.5
2028 | 30% | 0.95 | 40.4
2029 | 36% | 0.87 | 46.5
2030 | 43% | 0.77 | 52.4
2031 | 50% | 0.68 | 56.3
2032 | 57% | 0.58 | 59.1
2033 | 64% | 0.5 | 60.6
2034 | 70% | 0.43 | 61.7
2035 | 74% | 0.37 | 62.3
R11-T22 City water demand and supply
Source: Report 11 (Part 11 research report) · 5. Water demand by city (MLD)
Note: City supply figures are [R] via the subagent's sources.
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 11 city water outputs.
Used to derive: DC share of city water supply.
City | MW 2030 | MLD 2030 | MW 2035 | MLD 2035 | City supply (MLD) | Data-centre share 2030 / 2035 | High-case 2035 MLD
Mumbai MMR | 2083 | 23.2 | 4499 | 26 | BMC about 4,100, against 4,600 demand (Oct 2026) | 0.57% / 0.63% | about 85
Hyderabad | 641 | 7.1 | 1587 | 9.2 | HMWSSB 545 MGD ≈ 2,478 | 0.29% / 0.37% | about 30
Chennai | 468 | 5.2 | 1426 | 8.2 | Metrowater 1,245 (Apr 2025, incl. tankers) | 0.42% / 0.66% | about 27
Delhi NCR | 452 | 5 | 1025 | 5.9 | DJB about 1,002 MGD target ≈ 4,555 (Delhi only) | 0.11% / 0.13% | about 19
Pune | 311 | 3.5 | 692 | 4 | PMC about 1,222 (older figure) | 0.29% / 0.33% | about 13
Bengaluru | 232 | 2.6 | 510 | 2.9 | BWSSB about 1,935 supplied (2,225 capacity) | 0.13% / 0.15% | about 10
Kolkata | 80 | 0.9 | 147 | 0.85 | KMC 1,654–2,045 (sources conflict) | about 0.05% | about 3
Visakhapatnam | 250 | 2.8 | 637 | 3.7 | GVMC 84.44 MGD = 383.86 | 0.73% / 0.96% | about 17 (4.4%)
R11-T23 Pipeline shares by city
Source: Report 11 (Part 11 research report) · 6. Where new capacity goes, city by city
Note: The pipeline shares (C&W, on the 3,633 MW city-sum basis) are below.
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Ch 11 city allocation (2026–30).
Used to derive: Where new MW go.
City | Pipeline MW | Share of pipeline
Mumbai | 1726 | 47.5%
Hyderabad | 710 | 19.5%
NCR | 387 | 10.7%
Chennai | 368 | 10.1%
Pune | 258 | 7.1%
Bengaluru | 100 | 2.8%
Kolkata | 84 | 2.3%
R11-T24 Illustrative city scores for allocation
Source: Report 11 (Part 11 research report) · 6. Where new capacity goes, city by city
Note: Illustrative scores used [E; substitute the chapter-10 values]:
Data basis: Illustrative / framework / author judgement
Used in atlas: Ch 11 city allocation (illustrative scores).
Used to derive: Softmax share of growth.
City | Score
Mumbai | 85
Chennai | 80
Hyderabad | 78
NCR | 72
Visakhapatnam | 70
Pune | 68
Bengaluru | 65
Kolkata | 50
R11-T25 City capacity forecast
Source: Report 11 (Part 11 research report) · 6. Where new capacity goes, city by city
Note: 2035: the 6,100 MW increment is allocated with α = 0.5, k = 8.
Data basis: Calculated (model output)
Used in atlas: Ch 11 city capacity outputs.
Used to derive: City MW 2030 and 2035.
City | H1 2026 [R] | 2030 base | 2035 base | 2035 high (indicative) | Share of national, 2035 base
Mumbai MMR (incl. Navi Mumbai) | 890 | 2083 | 4499 | about 7,700 | 41.7%
Hyderabad (incl. periphery) | 151 | 641 | 1587 | about 2,900 | 14.7%
Chennai | 214 | 468 | 1426 | about 2,600 | 13.2%
Delhi NCR (incl. Noida/Greater Noida) | 183 | 452 | 1025 | about 1,800 | 9.5%
Pune | 133 | 311 | 692 | about 1,200 | 6.4%
Visakhapatnam | 0 | 250 | 637 | about 1,500 | 5.9%
Bengaluru (incl. Mysuru spill-over) | 162 | 232 | 510 | about 850 | 4.7%
Kolkata | 22 | 80 | 147 | about 250 | 1.4%
Other (Jamnagar etc.) | – | 150 | 248 | about 0 (inside the figures above) | 2.3%
Total | 1789 | about 4,670 | about 10,770 | about 18,800 | 100%
R11-T26 Driver-based 2030 forecasts
Source: Report 11 (Part 11 research report) · 7. Demand drivers (regression)
Note: Driver-based forecasts for 2030 [M]:
Data basis: Calculated (model output)
Used in atlas: Ch 11 driver cross-check (text).
Used to derive: Demand-side view of 2030.
Driver model | 2030 MW
UPI (UPI +20%/yr) | 2.5 GW
Traffic | 3.7 GW
Cloud | 3.9–4.9 GW
Mean | about 3.7 GW
R11-T27 Integrated base-case table 2026–2035
Source: Report 11 (Part 11 research report) · 8. Integrated base-case table (2026–2035) [M]
Data basis: Calculated (model output)
Used in atlas: Ch 11 integrated table and KPIs.
Used to derive: Year-by-year base case.
Year | MW low / base / high | IT TWh | Facility TWh | % of India | Net MtCO₂ | Water, national MLD | Water, Mumbai / Chennai / Hyderabad MLD | Cumulative capex ₹ lakh crore (US$ bn) | ₹ crore/MW (air / AI) | ₹/GPU-hr H100-class
2026 | 1,950 / 2,000 / 2,100 | 9.6 | 14.5 | 0.75% | 7.1 | 28.7 | 14 / 3.5 / 2.0 | 0.28 (3.1) | 59 / 89 | 220
2027 | 2,250 / 2,500 / 2,850 | 12.3 | 18.2 | 0.89% | 8.3 | 34.5 | 16 / 4.0 / 3.0 | 0.65 (7.3) | 60 / 91 | 176
2028 | 2,650 / 3,100 / 3,800 | 15.5 | 22.6 | 1.04% | 9.4 | 40.4 | 19 / 4.4 / 4.3 | 1.11 (12.5) | 62 / 92 | 141
2029 | 3,100 / 3,850 / 4,950 | 19.6 | 28.2 | 1.22% | 10.8 | 46.5 | 21 / 4.8 / 5.7 | 1.71 (19.2) | 63 / 94 | 113
2030 | 3,600 / 4,700 / 6,400 | 24.7 | 35.1 | 1.43% | 12.4 | 52.4 | 23 / 5.2 / 7.1 | 2.42 (27.2) | 64 / 96 | 90
2031 | 4,200 / 5,700 / 8,200 | 30.5 | 43 | 1.64% | 13.7 | 56.3 | 24 / 6.0 / 7.6 | 3.27 (36.7) | 65 / 98 | 72
2032 | 4,800 / 6,850 / 10,300 | 37.2 | 52.1 | 1.87% | 15.1 | 59.1 | 25 / 6.8 / 8.1 | 4.28 (48.1) | 67 / 100 | 58
2033 | 5,450 / 8,100 / 12,800 | 44.7 | 61.7 | 2.08% | 16.4 | 60.6 | 25 / 7.4 / 8.5 | 5.41 (60.8) | 68 / 102 | 46
2034 | 6,100 / 9,450 / 15,600 | 53 | 72.6 | 2.30% | 17.2 | 61.7 | 26 / 7.8 / 8.9 | 6.67 (75.0) | 70 / 104 | 37
2035 | 6,800 / 10,800 / 18,800 | 61.5 | 83 | 2.47% | 17.8 | 62.3 | 26 / 8.2 / 9.2 | 7.97 (89.6) | 72 / 107 | 30
R11-T28 Calculator parameters and Monte Carlo distributions
Source: Report 11 (Part 11 research report) · 9. Parameter table for the calculator, with Monte Carlo distributions
Data basis: Proxy / estimate
Used in atlas: Ch 11 slider ranges and Monte Carlo band.
Used to derive: Uncertainty range.
Parameter | Symbol | Low | Base | High | Suggested distribution | Basis
Starting capacity (end-2025) | C₀ | 1500 | 1611 | 1700 | Uniform | R (MeitY / C&W / CBRE)
CAGR | g | 0.18 | 0.25 | 0.32 | Triangular(0.15, 0.25, 0.33) | M (fitted 0.279)
Logistic ceiling | K (MW) | 12000 | 25000 | 45000 | Lognormal, median 25 GW, 90% CI 12–45 GW | E
Logistic rate | r | 0.24 | 0.26 | 0.3 | Uniform(0.22, 0.32) | M
Logistic midpoint | t₀ | 2032.8 | 2035.3 | 2036 | Derived: t₀ = 2025 + ln(K/C₀ − 1)/r | M
Conversion, under construction | c_UC | 0.85 | 0.95 | 1 | Beta(19, 1.5) | R/M
Conversion, planned | c_P | 0.4 | 0.6 | 0.8 | Beta(6, 4) | R/M
Conversion, MoU / announced | c_A | 0.2 | 0.35 | 0.5 | Uniform | R (CEEW) / E
Lag | L (years) | 2 | 3 | 4 | Discrete {2: 0.4, 3: 0.45, 4: 0.15} | E
Forecast haircut (delivered/forecast) | h | 0.58 | 0.7 | 0.87 | Triangular | M (backtest)
Utilisation | u(2026→2035) | 0.50→0.58 | 0.55→0.65 | 0.60→0.72 | Triangular on the 2030 value (0.52, 0.60, 0.68) | E
PUE | PUE(2026→2035) | 1.52→1.42 | 1.50→1.35 | 1.50→1.30 | Triangular on 2030 (1.32, 1.42, 1.50) | R/E
Grid emission factor | EF (2026 / 2030 / 2035) | 0.71 / 0.69 / 0.65 | 0.70 / 0.62 / 0.535 | 0.69 / 0.55 / 0.45 | Triangular on 2030 (0.55, 0.62, 0.69) | R (CEA) / E
Clean share | c_clean (2026 / 2030 / 2035) | 0.25 / 0.32 / 0.40 | 0.30 / 0.43 / 0.60 | 0.35 / 0.60 / 0.85 | Triangular on 2030 | R (operators) / E
Learning exponent | b | 0.15 | 0.1 | 0.05 | Uniform(0.05, 0.15); LR = 1 − 2^(−b) | E
Equipment inflation | π | 0.02 | 0.04 | 0.07 | Triangular | R (T&T 5.5–9%) / E
Base build cost | C₂₀₂₅ (₹ crore/MW) | 50 | 58.4 | 69 | Triangular | R (T&T, C&W)
AI premium | a | 0.3 | 0.5 | 0.8 | Uniform | R (US) / E
GPU price decline | d (%/yr) | 10% | 20% | 30% | Triangular(0.10, 0.20, 0.30) | M
H100-class price, 2026 | P₀ (₹/hr) | 150 | 220 | 395 | Triangular | R
Bass innovation | p | 0.01 | 0.03 | 0.05 | Uniform | E (Dell'Oro analogue)
Bass imitation | q | 0.25 | 0.4 | 0.55 | Uniform | E
Dry/liquid ceiling | m | 0.7 | 0.85 | 0.95 | Uniform | E
WUE, evaporative | L/kWh | 1.5 | 1.8 | 2.5 | Triangular | R
WUE, adiabatic | L/kWh | 0.2 | 0.5 | 0.8 | Uniform | R
WUE, dry / liquid | L/kWh | 0 | 0.1 | 0.2 | Uniform | E
Allocation exponent | k | 4 | 8 | 12 | Uniform | M
Incumbency weight | α | 0.3 | 0.5 | 0.7 | Uniform | M
National demand growth | g_grid | 4.5% | 6.41% | 7.3% | Triangular | R (CEA EPS; 7.35% FY21–25)
FX rate | ₹/US$ | 88 | 89 | 92 | Uniform | E

## R12
Report 12 · Water and energy
28 tables. Source line under each title; "Note" gives the context sentence from the report.
R12-T01 Water definitions and metrics
Source: Report 12 (Part 12 research report) · 1. Direct (on-site) water › 1.1 Definitions and metrics
Data basis: Source-derived, verified
Used in atlas: Ch 12 definitions; Data register.
Used to derive: Report withdrawal and consumption separately.
Term | Definition | Unit | Label
Withdrawal | Water taken from any source (municipal, groundwater, tanker, STP-treated) | kL, m³ | [Verified: LBNL24; WRI]
Consumption | Withdrawal minus discharge; mostly evaporation and drift | kL | [Verified: LBNL24 — "permanently removed from the immediate water cycle"]
Discharge | Blowdown, RO reject, sanitary sewage returned | kL | [Proxy: water-balance convention]
WUE (site) | Annual site water ÷ annual IT energy. Microsoft: "annual liters of water used for humidification and cooling" ÷ IT kWh | L/kWh_IT | [Verified: MSFT; LBNL24]
WUE (source) | Site WUE plus water used to generate the electricity consumed | L/kWh_IT | [Verified: LBNL24 — "source WUE accounts for the water required to generate the electricity"]
Basis caveat | NTT computes WUE as withdrawal ÷ IT energy; Microsoft's 0.30 is described as a "withdrawal WUE" | — | [Verified: NTT; MSFT blog]
ISO/IEC 30134-9 | International WUE standard (site and source categories) | — | [Proxy: text not reviewed — obtain from ISO/BIS]
EU EED reporting (Delegated Reg. 2024/1364) | Sites ≥500 kW IT report total water input (W_IN, m³) and potable water input (W_IN-POT, m³); first returns due 15 Sep 2024, then 15 May 2025 and yearly | m³ | [Verified: EU24]
EU rating scheme (draft) | A–G energy and water labels auto-generated from 15 Aug 2027; water grade from freshwater intake ÷ IT energy | — | [Verified-secondary: EU24]
R12-T02 Cooling-tower water components and physics
Source: Report 12 (Part 12 research report) · 1. Direct (on-site) water › 1.2 Components and physics
Data basis: Proxy / estimate
Used in atlas: Ch 12 "Inside a cooling tower" calculator.
Used to derive: Tower WUE vs cycles of concentration.
Component | Formula / rule | Low | Typical | High | Unit | Label
Latent heat of vaporisation | h_fg | 2,257 (100 °C) | 2,430 (30 °C) | 2,450 (20 °C) | kJ/kg | [Proxy: steam tables]
Pure-evaporation water per kWh of heat | 3,600 ÷ h_fg | 1.47 | 1.48 | 1.6 | L/kWh_th | [Model]
Latent share of tower heat rejection | f_lat | 0.75 | 0.85 | 0.95 | — | [Proxy: tower practice]
Evaporation | E = Q_rej × f_lat × 3,600/h_fg | 1.1 | 1.26 | 1.5 | L/kWh_th | [Model]
Heat rejected per kWh IT (water-cooled chillers) | 1 + compressor + pump/fan heat | 1.15 | 1.25 | 1.35 | kWh_th/kWh_IT | [Proxy: chiller COP 5–7]
Blowdown | B = E ÷ (CoC − 1) | E/9 (CoC 10) | E/3 (CoC 4) | E/1 (CoC 2, hard water) | L/kWh_th | [Model]
Drift | 0.001–0.005% of circulation (~86 L/kWh_th at ΔT 10 K) | 0.0009 | 0.002 | 0.004 | L/kWh_th | [Model: 3,600/(4.19×10)]
Tower make-up | M = E + B + D | 1.3 | 1.7 | 3 | L/kWh_th | [Model]
Tower-based WUE | M × Q_rej/IT | 1.5 | 2.1 | 3.5 | L/kWh_IT | [Model]; NTT evaporative 1.42–2.93 [Verified: NTT]
Humidification (air-cooled halls) | — | 0 | 0.01 | 0.05 | L/kWh_IT | [Proxy: LBNL24 "occasional humidification"]
RO reject | feed × (1 − recovery); recovery 65–80% | 0.25 | 0.4 | 0.55 | L per L permeate | [Proxy]
Domestic/sanitary | 45 L/person/day × staff | 0.005 | 0.01 | 0.02 | L/kWh_IT at >10 MW | [Proxy: NBC/CPHEEO norms]
Landscaping | 2–5 L/m²/day of green area | — | — | — | — | [Proxy; use STP water]
DG radiator cooling | Closed loop | 0 | ~0 | ~0 | — | [Proxy]
Fire systems | One-time fill plus tests; storage per NBC/TAC | — | — | — | kL storage | [Proxy: NBC Part 4]
R12-T03 Published WUE and water values
Source: Report 12 (Part 12 research report) · 1. Direct (on-site) water › 1.3 Published WUE and water values
Data basis: Source-derived, verified
Used in atlas: Ch 12 power-vs-water chart (fleet dots); Data register verified figures.
Used to derive: Benchmark WUE/PUE.
Entity / scope | Value | Year | Label
US all data centres, average site WUE | ~0.36 L/kWh through 2023; 0.45–0.48 after 2023 | 2023 / 2028 | [Verified: LBNL24]
US direct water consumption | 66 billion L (2023); 21.2 billion L (2014); hyperscale 60–124 billion L in 2028 | — | [Verified: LBNL24]
US hyperscale aggregate median WUE | 0.32 L/kWh (0.40 if adiabatic runs at 0.2) | 2023 | [Verified: LBNL24]
Hyperscale adiabatic systems (self-reported) | 0.1–0.3 L/kWh | — | [Verified: LBNL24]
Microsoft global WUE / PUE | 0.30 / 1.16 (FY24); 0.27 / 1.17 (FY25) | FY24–25 | [Verified: MSFT]
Microsoft Asia-Pacific WUE / PUE | 0.03 / 1.25 (FY24); 0.25 / 1.28 (FY25) | FY24–25 | [Verified: MSFT]
Microsoft zero-water-for-cooling design | Avoids >125 million L/yr per datacenter | from Aug 2024 | [Verified: MSFT blog]
Microsoft India sites | On-site WUE 0.000 L/kWh (dry cooling) in Li et al.'s table | — | [Verified: LI]
Google fleet PUE | 1.09 (2025) | 2025 | [Verified: GOOG25]
Google WUE used in Gemini analysis | 1.15 L/kWh (fleet) | 2024 | [Verified-secondary: MDPI reconstruction of GOOG25]
NTT DATA WUE, whole portfolio | 1.01 / 0.65 / 0.72 L/kWh | FY22 / 23 / 24 | [Verified: NTT]
NTT DATA WUE, evaporative sites | 2.93 / 2.77 / 1.42 L/kWh | FY22 / 23 / 24 | [Verified: NTT]
NTT DATA PUE | 1.40 / 1.38 / 1.38 | FY22 / 23 / 24 | [Verified: NTT]
Equinix global / evaporative sites WUE | 0.91 / 1.41 L/kWh | 2025 | [Verified-secondary: Equinix 2025 report via Wikipedia]
CtrlS total water | 409,037 kL (2023-24) vs 468,330 kL (2022-23); no WUE | — | [Verified: DTE]
Nxtra, CtrlS | No published WUE | 2025 | [Verified: DTE]
Yotta | Claims "extremely low WUE", no number | 2025 | [Verified: DTE]
India sector | DCs ≈ 0.5% of national electricity (2025); ~271 DCs (Jan 2026); a 100 MW hyperscale "can take ~2 million litres of water per day" | 2025–26 | [Verified: CEEW]
India sector share of water | ~0.02–0.03% of national water demand | 2025 | [Verified-secondary: CEEW author in Scroll]
India siting | ~75% of DCs in water-stressed regions; ~25 million L per MW per year | 2026 | [Verified-secondary: DTE Apr 2026 via Substack]
R12-T04 Water per AI query
Source: Report 12 (Part 12 research report) · 1. Direct (on-site) water › 1.4 Water per AI query
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 12 "Water behind one AI prompt" chart.
Used to derive: Per-prompt water with grid water.
Estimate | Energy | Water | Scope | Label
Google Gemini median text prompt (May 2025) | 0.24 Wh | 0.26 mL (0.15 mL narrow method); 0.03 gCO₂e | On-site only | [Verified: GOOG25]
OpenAI average ChatGPT query (Altman, Jun 2025) | 0.34 Wh | ~0.32 mL | Undisclosed method | [Verified-secondary: Towards Data Science]
Li et al., GPT-3 medium request, India | — | 19.7 mL (0 on-site + 19.7 off-site); 25.4 requests per 500 mL; PUE 1.430, EWIF 3.445 L/kWh | On-site + grid | [Verified: LI]
Gemini-like prompt, dry-cooled Indian DC | 0.24 Wh | 0.24×10⁻³ kWh × (0.03 + 3.0) = 0.73 mL | On-site + grid | [Model]
Same, evaporative Indian DC | 0.24 Wh | 0.24×10⁻³ × (2.0 + 3.0) = 1.2 mL | On-site + grid | [Model]
R12-T05 Water intensity of electricity generation
Source: Report 12 (Part 12 research report) · 2. Indirect (off-site) water › 2.1 Water intensity of generation
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 12 "Where grid water comes from" chart.
Used to derive: Water intensity by generation source.
Technology | Consumption | Withdrawal | Label
Indian coal, once-through (legacy) | small | 70–200 m³/MWh (CSE); 80–160 m³/MWh | [Verified: PowerLine/CSE; SD23]
Indian coal, closed-loop towers (actual) | 2.8–3.4 m³/MWh, about twice the world average of 1.2–1.5 | ~4 m³/MWh average (CSE) | [Verified: SD23; PowerLine/CSE]
MoEFCC norm, existing CT plants | ≤3.5 m³/MWh (by 7 Dec 2017) | — | [Verified: MOEF15]
MoEFCC norm, plants after 1 Jan 2017 | 2.5 m³/MWh with ZLD (2015), relaxed to 3.0 m³/MWh in June 2018 | — | [Verified: MOEF15 amendments]
FGD additional consumption | ~0.3 m³/MWh | — | [Verified: PowerLine/CSE]
Coal with air-cooled condenser | 0.45–0.65 m³/MWh | — | [Verified: SD23]
Nuclear with towers (US median) | 672 gal/MWh = 2.54 L/kWh | higher than coal | [Verified: NREL]
Tower-cooled thermal, upper bound | ~1,000 gal/MWh ≈ 3.8 L/kWh | — | [Verified: NREL]
Gas CCGT with tower | ~0.7–0.8 L/kWh | ~1 L/kWh | [Proxy: NREL medians via secondary sources]
Hydro, reservoir evaporation (contested) | ~17 L/kWh gross; NREL excludes hydro "due to the wide range of estimates" | — | [Verified-secondary: NREL caption + citing literature]
Solar PV (cleaning) | <0.19 L/kWh; Indian dry robots lower | — | [Verified-secondary: NREL-derived]
Wind | ~0 | ~0 | [Verified: NREL]
Coastal seawater once-through plants | Freshwater ≈ 0 | Seawater 70–200 L/kWh | [Proxy: per plant]
R12-T06 Indian grid-average water intensity, FY25
Source: Report 12 (Part 12 research report) · 2. Indirect (off-site) water › 2.2 Indian grid-average water intensity
Note: Generation base for FY2024-25: total 1,824 BU, thermal 1,363 BU (74.7%) [Verified: CREA], and RE 403.64 BU (22.13%, which appears to include large hydro) [Verified: MNRE25]. Nuclear is the residual, about 3%; large hydro about 8% [Proxy: residual allocation].
Data basis: Calculated (model output)
Used in atlas: Ch 12 grid-water chart and calculator default (3.0 L/kWh).
Used to derive: Indian grid water intensity.
Source | Share | Consumption intensity (L/kWh) | Contribution (L/kWh generated)
Coal and lignite | 73% | 3.0 (2.8–3.4) | 2.19
Gas | 1.5% | 0.7 | 0.01
Nuclear | 3% | 2.5 | 0.08
Solar, wind, bio | 14% | 0.1 | 0.01
Large hydro | 8% | 0 (operational) – 17 (gross evaporation) | 0 – 1.36
Total at busbar | 100% | — | 2.29 – 3.65
At consumer meter (÷ (1 − 17% losses) [Proxy]) | — | — | 2.76 – 4.40
R12-T07 State grid water proxies
Source: Report 12 (Part 12 research report) · 2. Indirect (off-site) water › 2.2 Indian grid-average water intensity
Note: State proxies (replace with SLDC/CEA mix and plant water data):
Data basis: Proxy / estimate
Used in atlas: Ch 12 state ranges chart and calculator grid options.
Used to derive: State grid water.
State | Grid water proxy (L/kWh delivered) | Basis | Label
Karnataka | 1.5–2.2 | RE was 48.10% of state generation in 2024-25 | [Verified: MNRE25 share]; [Proxy: intensity]
Tamil Nadu | 1.8–2.6 | High wind/solar; seawater-cooled coastal plants | [Proxy]
Andhra Pradesh | 2.0–3.0 | Coastal seawater plus inland coal | [Proxy]
Maharashtra | 2.8–3.4 | Coal-heavy MSEDCL portfolio | [Proxy]
Telangana | 2.8–3.4 | Coal-heavy | [Proxy]
Uttar Pradesh | 3.0–3.6 | Coal-heavy, inland freshwater | [Proxy]
R12-T08 Source WUE by case
Source: Report 12 (Part 12 research report) · 2. Indirect (off-site) water › 2.3 Source WUE formula
Note: Contracted mix: EWIF_eff = Σ (share_i × EWIF_i); RE-RTC (solar + wind + BESS) ≈ 0.05–0.15 L/kWh [Proxy: NREL]
Data basis: Calculated (model output)
Used in atlas: Ch 12 source WUE in power-vs-water view.
Used to derive: Total water per kWh of IT.
Case | WUE_site | PUE | EWIF | Source WUE
Mumbai evaporative colo, grid | 2 | 1.5 | 3 | 6.5
Hyderabad adiabatic hyperscale, grid | 0.45 | 1.3 | 2.8 | 4.09
Bengaluru DLC dry-cooled AI, grid | 0.03 | 1.25 | 1.8 | 2.28
Same, 90% RE-RTC (0.1) + 10% grid (1.8) → EWIF 0.27 | 0.03 | 1.25 | 0.27 | 0.37
R12-T09 Embedded water (scope 3)
Source: Report 12 (Part 12 research report) · 2. Indirect (off-site) water › 2.4 Embedded water (scope 3), order of magnitude
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Reference only (scope 3 water).
Used to derive: Embedded water share.
Item | Value | Label
Global DC water 2023 (IEA): 560 billion L = 373 indirect + 140 direct + 47 hardware manufacturing | — | [Verified-secondary: IEA via gpusmith]
Hardware manufacturing share | ~8% | [Model: 47/560]
Concrete for a 100 MW campus | ~100,000–200,000 m³ × ~150–200 L/m³ ≈ 15–40 ML, one-time | [Proxy: construction norms]
Takeaway | Embedded water ≈ 1–3 years of a dry-cooled site's direct water, but under 5% of its grid water | [Model]
R12-T10 Water and energy by cooling technology (India)
Source: Report 12 (Part 12 research report) · 3. Water by cooling technology
Note: Annual averages for Indian climates [Proxy: engineering ranges cross-checked against LBNL24's ranking and operator data where noted].
Data basis: Proxy / estimate
Used in atlas: Ch 12 power-vs-water boxes; calculator design defaults.
Used to derive: PUE and WUE ranges per technology.
Technology | WUE site (L/kWh_IT) | Annual PUE (India) | Energy penalty | Climate driver | Capex | Maturity
Water-cooled chillers + open towers | 1.5–2.5 (to 3.5 at low CoC) | 1.35–1.60 | baseline | Wet-bulb (coastal design WB ~28–29 °C) | baseline | Mature; highest WUE per LBNL24
Waterside economiser + towers (liquid IT) | 1.0–2.0 | 1.15–1.35 | lower | Wet-bulb | +0–10% | Mature; LBNL: "consumes substantial amounts of water"
Air-cooled chillers | ~0–0.05 | 1.45–1.75 | +8–15% | Dry-bulb; 45 °C+ Delhi peaks derate | −5 to −10% | Mature; LBNL: "use no water, they use more energy"
Dry coolers (no adiabatic) + chiller trim | ~0–0.05 | 1.30–1.55 air IT; 1.10–1.25 liquid IT | + air IT; ~0 W32–W45 | Dry-bulb | +5–15% | Mature
Adiabatic / hybrid dry coolers | 0.2–0.8 | 1.20–1.40 | small | Wet mode above ~26–30 °C dry-bulb | +10–20% | Mature
Direct evaporative (air-side) | 0.3–1.2 | 1.10–1.25 | low | Needs low WB and clean air | +0–10% | Limited Indian fit
Indirect evaporative (IEC) | 0.3–1.0 | 1.15–1.30 | low | WB; no outside air in hall | +15–30% | Mature
Rear-door heat exchangers | per heat-rejection plant | 1.20–1.40 | — | Facility water temperature | +per rack | Mature to 40–70 kW/rack
Direct-to-chip single-phase + dry coolers | 0–0.05 | 1.10–1.25 | low | Dry-bulb vs W32–W45 | +15–30% | Mainstream for GB200 (NVL72 ~120 kW/rack) [Verified: NVDA]
Direct-to-chip two-phase | 0–0.05 | 1.08–1.20 | low | Dry-bulb | Higher | Early commercial
Immersion single-phase | 0–0.05 | 1.05–1.15 | lowest fans | Dry-bulb | +20–40% | Growing
Immersion two-phase | 0–0.05 | 1.03–1.10 | lowest | Dry-bulb | Highest; fluorocarbon risk | Niche
Seawater / lake once-through | ~0 freshwater | 1.15–1.30 | low | Sea 27–31 °C off India | High (CRZ, intake/outfall) | CEEW: coastal hyperscalers "leverage seawater cooling" [Verified: CEEW]
Air-side economiser (free cooling) | ~0 | 1.15–1.30 in Bengaluru/Pune winters | — | Dry-bulb below ~24–27 °C | Low | Limited hours
R12-T11 Wet-mode hours and design wet-bulb by city
Source: Report 12 (Part 12 research report) · 3. Water by cooling technology
Note: Hours of adiabatic/IEC wet mode per year (above ~28 °C dry-bulb) [Proxy: climatology; replace with ISHRAE TMY]:
Data basis: Proxy / estimate
Used in atlas: Ch 12 wet-hours chart; checked by the 8,760-hour model.
Used to derive: Adiabatic water by city.
City | Wet-mode hours/yr | Tower design WB (0.4%) | Notes
Bengaluru | 1,000–1,800 | ~23–24 °C | Best Indian climate for dry/adiabatic
Pune | 1,800–2,800 | ~24–25 °C | Good
Hyderabad | 3,000–4,000 | ~25–26 °C | Dry heat suits adiabatic; spiky April–May
Delhi NCR | 3,000–3,800 | ~28 °C | 45 °C+ peaks; humid monsoon
Mumbai | 3,500–5,000 | ~28 °C | Humidity cuts adiabatic gain
Chennai | 5,000–6,500 | ~28–29 °C | STP/seawater key
Kolkata | 3,500–4,500 | ~29 °C | Hot-humid
Visakhapatnam | 4,500–6,000 | ~28–29 °C | Seawater option
R12-T12 Peak water factors
Source: Report 12 (Part 12 research report) · 4. Peak water demand › 4.1 Peak factors (calculator inputs)
Data basis: Calculated (model output)
Used in atlas: Ch 12 "Peaks size the pipes" chart; calculator peak factors.
Used to derive: Peak-day and peak-hour water.
System | Peak-month / avg | Peak-day / avg | Peak-hour / avg hour | Peak season | Label
Towers, Mumbai/Chennai | 1.10–1.25 | 1.3–1.6 | 1.5–1.9 | Apr–May; Oct | [Model: Example A]
Adiabatic/hybrid, Hyderabad/Delhi | 1.8–2.5 | 2.0–2.5 | 3.5–5.0 | Apr–Jun | [Model: Example B]
Adiabatic, monsoon months | 0.3–0.6 | — | — | Jul–Sep | [Model]
Dry/DLC (domestic only) | 1.0–1.1 | 1.1–1.3 | 2–3 | — | [Proxy]
R12-T13 IT load profile archetypes
Source: Report 12 (Part 12 research report) · 5. Hourly water and electricity profiles › 5.1 IT load profile archetypes
Data basis: Source-derived, verified
Used in atlas: Ch 12 utilisation assumptions.
Used to derive: Average IT load by archetype.
Archetype | Avg / design IT | Diurnal swing | Sub-minute behaviour | Label
Enterprise/colo | 60–80% (lease fill); colo server utilisation 21% (2014) → 35% (2027) | ±3–8% | Smooth | [Verified: LBNL24]; [Proxy: fill]
Hyperscale cloud | 70–85%; utilisation 45% → 50% | ±5–10% | Smooth | [Verified: LBNL24]; [Proxy]
AI training | 80% operational time at ~70% of rated; saturated 8×H100 node 7.9 kW (~78%) | Flat | "Square-wave" drops at synchronisation | [Verified: LBNL24]
AI inference | 40% operational time; power half of training | Diurnal | Bursty | [Verified: LBNL24]
Idle floor | AI ~20% of rated; conventional 36% of max (2023) → 27% (2028) | — | — | [Verified: LBNL24]
R12-T14 Hot-day hourly profile: 50 MW Hyderabad, adiabatic
Source: Report 12 (Part 12 research report) · 5. Hourly water and electricity profiles › 5.3 Hot-day profile: 50 MW hyperscale, Hyderabad, adiabatic (Example B), May design day
Note: IT is held at a flat 42 MW [Proxy]. Temperatures follow a sinusoid from 27 °C at 05:00 to 40 °C at 15:00 [Proxy: replace with ISHRAE TMY]. IEX prices are shaped to June 2026 averages: trough ₹1.17 at 11:00, peak ₹9.90 at 22:30, 08–16 h average ₹1.63, 18–23 h average ₹8.10 [Verified-secondary: earthsync; Proxy: shape]. Shown every two hours; totals come from the full 24-hour model.
Data basis: Calculated (model output)
Used in atlas: Ch 12 "One hot day, hour by hour" chart.
Used to derive: Hourly water, power and price; dry-at-noon saving.
Hour | T_db (°C) | PUE | Facility MW | WUE (L/kWh_IT) | Water (kL/h) | IEX DAM proxy (₹/kWh)
0 | 31 | 1.31 | 55 | 0.64 | 26.9 | 6
2 | 29 | 1.28 | 53.8 | 0.42 | 17.6 | 4
4 | 27.5 | 1.26 | 52.8 | 0.26 | 10.9 | 3.8
6 | 28 | 1.27 | 53.1 | 0.31 | 13 | 4.5
8 | 32 | 1.33 | 55.7 | 0.74 | 31.1 | 2.2
10 | 36 | 1.39 | 58.2 | 1.17 | 49.1 | 1.3
12 | 38.5 | 1.42 | 59.7 | 1.44 | 60.5 | 1.2
14 | 40 | 1.45 | 60.7 | 1.6 | 67.2 | 1.5
16 | 39 | 1.43 | 60.1 | 1.49 | 62.6 | 3
18 | 35.5 | 1.38 | 57.9 | 1.12 | 47 | 6.5
20 | 33 | 1.34 | 56.3 | 0.85 | 35.7 | 9
22 | 32 | 1.33 | 55.7 | 0.74 | 31.1 | 9.9
Day (24 h) | — | avg 1.347 | 1,357.7 MWh | avg 0.90 | 905.9 kL | —
R12-T15 Tariff time-of-day structures
Source: Report 12 (Part 12 research report) · 5. Hourly water and electricity profiles › 5.4 Tariff time structures
Data basis: Source-derived, verified
Used in atlas: Ch 12 hourly context; Ch 5 load shift.
Used to derive: ToD saving potential.
State | ToD rule for HT | Label
Telangana (FY26) | +₹1.00/unit 06–10 and 18–22; −₹1.50/unit 22–06 | [Verified: TGERC]
Maharashtra (FY26–30) | HT industrial/commercial ToD charge 25%; solar-hour rebates from −15% (FY26) | [Verified: MERC]
Grid emission factor | Lowest in solar hours, highest in evening; India weighted average declined from 0.774 tCO₂/MWh (FY2013-14) to 0.710 tCO₂/MWh in FY2024-25 (1,234.19 MT ÷ 1,739.06 BU) | [Verified: CEA CO2 Baseline Database User Guide V21.0, Nov 2025]
R12-T16 DISCOM HT/EHT tariffs, FY2025-26
Source: Report 12 (Part 12 research report) · 6. Grid electricity options in India › 6.1 DISCOM HT/EHT tariffs (FY2025-26 unless noted)
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 12 cost-vs-water chart (landed ₹/kWh).
Used to derive: Landed power cost by state and category.
State / DISCOM | Category | Energy charge | Demand charge | Other | Label
Maharashtra MSEDCL | HT-I(A) industry | ₹7.48/kVAh (FY26); then 7.27, 7.11 | ₹555/kVA/mo (then 560, 565) | Wheeling ~₹0.62 HT; 10% wheeling discount for DCs on OA or green tariff | [Verified: MERC]; a secondary claim of ₹8.68/kVAh after the Mar 2026 review is unverified
Maharashtra MSEDCL | HT-II commercial | ₹9.26 + ₹0.62 = ₹9.88/kVAh | ₹555/kVA/mo | — | [Verified: MERC]
Mumbai TPC-D | HT-II / EHV commercial | ₹5.89 + ₹0.69 wheeling / ₹5.89 | ₹300/kVA/mo | Green power tariff ₹0.25/kWh | [Verified: MERC TPC-D]
Telangana TGSPDCL | HT-I(A) industry | ₹7.65 / 7.15 / 6.65 per kVAh (11 / 33 / ≥132 kV) | ₹500/kVA/mo | Green tariff ₹0.66/unit | [Verified: TGERC]
Telangana TGSPDCL | HT-II(A) commercial | ₹8.80 / 8.00 / 7.80 per kVAh | ₹500/kVA/mo | — | [Verified: TGERC]
Karnataka (all ESCOMs) | HT-2(a) industry | 660 paise/kWh (FY26, FY27); 650 (FY28) | ₹345 / 350 / 355 per kVA/mo | P&G surcharge 36 paise (FY26), 35 (FY27); BESCOM true-up +56 paise (May 2026–Apr 2027) | [Verified: KERC; true-up Verified-secondary]
Tamil Nadu TNPDCL | HT-I (incl. IT) / HT-III commercial | ₹7.50 / ₹9.40 per kWh | ₹608/kVA/mo | Wheeling HT ₹1.04/kWh | [Verified-secondary: TNERC summary]
R12-T17 Open access and procurement options
Source: Report 12 (Part 12 research report) · 6. Grid electricity options in India › 6.2 Open access and procurement options
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 12 cost-vs-water chart (procurement options).
Used to derive: Landed cost of each procurement route.
Option | Key conditions | Generation price | Adders | Carbon / water | Label
DISCOM green tariff | Premium over normal tariff | — | +₹0.25 (TPC-D), +₹0.66 (Telangana) | RE attribute; physical grid water unchanged unless additional RE | [Verified: MERC TPC-D; TGERC]
GEOA Rules 2022 | Threshold 100 kW; CSS may not rise >50% over 12 years from grant year; additional surcharge not applicable if consumer pays fixed charges; monthly banking ≥30% of consumption | — | CSS, wheeling, transmission, losses, banking | Additional RE → EWIF ~0.1 | [Verified: GEOA gazette]; 100 kW [Proxy: verify amendment]
FOR model GEOA regulations | CSS shall not exceed 20% of tariff or ABR | — | — | — | [Verified: GEOA FOR]
CSS, Telangana FY26 | HT-I ₹1.82 / 1.56 / 1.46; HT-II(A) ₹2.15 / 1.86 / 1.79 per kWh (11 / 33 / 132 kV) | — | — | — | [Verified: TGERC]
CSS, Tamil Nadu | Industrial ₹1.99/kWh; commercial ₹2.57/kWh | — | — | — | [Verified-secondary: TNERC summary]
Additional surcharge, Karnataka | BESCOM proposed ₹1.65/kWh (not approved) | — | — | — | [Verified-secondary: SolarQuarter]
TN banking | 8% of banked energy, in kind (TN GEOA Regs 2025) | — | — | — | [Verified-secondary: SolarQuarter]
Group captive | ≥26% equity, ≥51% consumption (Electricity Rules 2005); CSS/AS exempt | ₹4.0–5.25 | Wheeling, transmission, losses, banking | Near-zero water if RE | [Proxy: rules]; TN exemption [Verified-secondary]
ISTS RE / FDRE via third party | ISTS charges levied at 25% for COD Jul 2025–Jun 2026, 50%, 75%, then 100% after 1 Jul 2028; waiver worth ₹0.4–1.8/unit per industry | FDRE-RTC ₹5.25; 4-h peak ₹5.99; RTC-IV ₹5.06–5.07; SJVN FDRE-3 ₹4.82–4.91 | ISTS + state charges + CSS + AS | Near-zero water | [Verified: ISTS; SECI; SaurEnergy]
IEX G-DAM | FY25 weighted avg ₹4.01/unit; Jan 2026 ₹4.06; Feb 2026 ₹3.43 | — | OA charges + fees | RE attribute | [Verified: IEX]
IEX DAM | Jan 2026 ₹3.86; Feb 2026 ₹3.58 | — | — | Grid mix | [Verified: IEX]
On-site solar | Rooftop ≈ 0.1–0.3 MWp per MW IT; negligible for large sites | ₹3–4.5/kWh | Maharashtra GSC ₹1.40/unit HT | — | [Proxy]; GSC [Verified-secondary: MERC order]
Captive gas / DG | Backup only; DG ₹25–35/kWh (diesel ~₹90/L × 0.27 L/kWh) | — | — | High CO₂ | [Model]
RECs / I-RECs | Unbundled; no physical additionality | — | — | No physical water change | [Proxy]
Carbon Credit Trading Scheme | DCs not yet obligated entities (as understood) | — | — | — | [Proxy: verify with BEE]
R12-T18 Supply voltage by facility size
Source: Report 12 (Part 12 research report) · 6. Grid electricity options in India › 6.3 Reliability and connection
Data basis: Proxy / estimate
Used in atlas: Ch 12 calculator contract demand note.
Used to derive: Supply voltage per project size.
MW (facility) | Typical supply voltage | Label
<5 MVA | 11 kV | [Proxy: state supply codes]
5–20 MVA | 33 kV | [Proxy]
20–60 MVA | 66/110/132 kV | [Proxy]
60–200 MVA | 132/220 kV | [Proxy]
>200 MVA | 220/400 kV, ISTS or dedicated substation | [Proxy]
R12-T19 Typical energy parameter values
Source: Report 12 (Part 12 research report) · 7. Energy calculations › 7.2 Typical parameter values
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Ch 12 calculator parameters.
Used to derive: Energy, MVA, DG and UPS sizing.
Parameter | Low | Typical | High | Label
Global average PUE | 1.54 (2025) | 1.56 (2024) | 1.58 (2023) | [Verified: UPT25; Uptime blog]
New facilities / >20 MW | 1.44 (>20 MW) | 1.48 (last 5 yrs) | — | [Verified: UPT25 — "Facilities commissioned within five years of the survey (from around early 2020) achieved an average PUE of 1.48"]
US modelled average PUE | 1.15–1.35 (2028) | 1.4 (2023) | 1.6 (2014) | [Verified: LBNL24]
Hyperscaler fleets | 1.09 (Google 2025) | 1.17 (Microsoft FY25) | 1.28 (MSFT APAC FY25) | [Verified: GOOG25; MSFT]
Indian colo PUE | 1.35 | 1.45–1.55 | 1.7 | [Verified: Uptime Field Report 183 — Asia-Pacific (excl. China) average annual PUE 1.52 (n=79) vs global 1.54; Proxy for India range]
UPS efficiency | 77–85% (edge) | 80–94% (colo) | 90–99% (hyperscale/AI) | [Verified: LBNL24]
Transformer loss per stage | 0.5% | 1.0% | 1.5% | [Proxy]
Power factor | 0.95 | 0.98 | 0.99 | [Proxy]
Rack density | most 10–30 kW; few >30 kW | — | AI 120–142 kW | [Verified: UPT25; NVDA]
DGX H100 (8 GPU) rated | 10.2 kW | — | — | [Verified: LBNL24]
DGX B200 max | 14.3 kW | — | — | [Verified: NVDA]
GB200 NVL72 rack | ~120 kW (NVIDIA) | 132 kW (HPE nominal) | GB300: 135–142 kW | [Verified-secondary: NVDA summaries]
AI annualised power | 60–80% of rated | 70% | — | [Verified: LBNL24]
Energy per AI prompt | 0.10 Wh (narrow) | 0.24 Wh (Gemini) | 0.34 Wh (ChatGPT avg) | [Verified: GOOG25; secondary for OpenAI]
R12-T20 Scale snapshot by archetype
Source: Report 12 (Part 12 research report) · 7. Energy calculations › 7.3 Scale snapshot
Data basis: Calculated (model output)
Used in atlas: Reference for Ch 12 calculator.
Used to derive: Energy and connection per archetype.
Archetype | IT design | Utilisation | IT MU/yr | PUE | Facility MU/yr | Contract MVA | DG fuel at full load (L/h)
5 MW enterprise (Pune) | 5 MW | 60% | 26.3 | 1.6 | 42 | 9 | 2300
20 MW colo (Mumbai) | 20 MW | 70% | 122.6 | 1.5 | 184 | 35 | 8600
50 MW hyperscale (Hyderabad) | 50 MW | 80% | 350.4 | 1.3 | 455.5 | 76 | 18900
100 MW AI campus (Bengaluru) | 100 MW | 75% | 657 | 1.25 | 821.3 | 150 | 35100
R12-T21 Example A: 20 MW Mumbai colo, step by step
Source: Report 12 (Part 12 research report) · 8. Worked examples › Example A: 20 MW IT colocation, Mumbai (Navi Mumbai), water-cooled chillers + open cooling towers
Data basis: Calculated (model output)
Used in atlas: Ch 12 "Where the water goes" and cost-vs-water charts (Example A).
Used to derive: Water and cost for a Mumbai colo.
Step | Calculation | Result | Label
Average IT | 20 MW × 70% | 14 MW | [Proxy: colo fill]
IT energy | 14 × 8,760 | 122,640 MWh = 122.6 MU | [Model]
PUE | Hot-humid tower plant | 1.5 | [Proxy: Uptime 1.54 avg]
Facility energy | 122,640 × 1.5 | 183,960 MWh ≈ 184 MU | [Model]
Site WUE | 1.25 × 0.85 × 1.48 = 1.57 evaporation + CoC-4 blowdown 0.52 ≈ 2.1 → use 2.0 | 2.0 L/kWh | [Model; NTT 1.42–2.93 Verified]
Direct water | 122.64 M kWh × 2.0 | 245,280 kL/yr = 0.67 MLD average | [Model]
Indirect water | 183.96 M kWh × 3.0 | 551,880 kL/yr | [Model]
Total water | — | 797,160 kL/yr (source WUE 6.5) | [Model]
Peak day | 20 MW × 24 h × 2.2 L/kWh | 1,056 kL/day (1.57× average) | [Model]
Peak hour | 20,000 kWh × 2.3 | 46 kL/h | [Model]
Storage (48 h at peak) | 46 × 48 | ~2,200 kL | [Model]
Contract demand | 20 × PUE_peak 1.65 = 33 MW ÷ 0.95 | ~35 MVA (110/220 kV) | [Model]
DG fuel | 33,000 kW × 0.26 | 8,580 L/h; 24 h = 206 kL | [Model]
R12-T22 Example A: landed electricity cost by option
Source: Report 12 (Part 12 research report) · 8. Worked examples › Example A: 20 MW IT colocation, Mumbai (Navi Mumbai), water-cooled chillers + open cooling towers
Note: Landed electricity cost (184 MU; 35,000 kVA):
Data basis: Calculated (model output)
Used in atlas: Ch 12 cost-vs-water chart (Example A dots).
Used to derive: Cheapest procurement route.
Option | Calculation | ₹ crore/yr | ₹/kWh | Label
1. MSEDCL HT-I industry (if DC gets industrial status) | 184 × (7.48 + 0.62) = 149.0 + demand 35,000 × 555 × 12 = 23.3 | 172.3 | 9.37 | [Model on MERC rates; excl. duty, ToD]
1b. MSEDCL HT-II commercial | 184 × 9.88 = 181.8 + 23.3 | 205.1 | 11.15 | [Model]
2. HT-I + green tariff (₹0.25 TPC-D benchmark) | +184 × 0.25 = 4.6 | 176.9 | 9.62 | [Model; MSEDCL premium not confirmed]
3. Group-captive RE-RTC (intra-state) | 5.25 + wheeling 0.62 + transmission/losses ~0.6 + banking ~0.2 = 6.67 × 184 = 122.7 + 23.3 | 146 | 7.94 | [Model; adders Proxy]
4. Third-party ISTS FDRE | 5.25 + ISTS ~0.6 + 0.62 + CSS ~1.8 [Proxy] + losses 0.4 = 8.67 × 184 = 159.5 + 23.3 | 182.8 | 9.94 | [Model]
R12-T23 Example B: 50 MW Hyderabad hyperscale, step by step
Source: Report 12 (Part 12 research report) · 8. Worked examples › Example B: 50 MW IT hyperscale, Hyderabad, air-side economiser / adiabatic-assisted cooling
Data basis: Calculated (model output)
Used in atlas: Ch 12 charts (Example B) and hourly profile.
Used to derive: Water and cost for a Hyderabad hyperscale site.
Step | Calculation | Result | Label
Average IT | 50 × 80% | 40 MW | [Proxy]
IT energy | 40 × 8,760 | 350,400 MWh | [Model]
PUE annual | — | 1.3 | [Proxy: MSFT APAC 1.25–1.28 Verified]
Facility energy | 350,400 × 1.30 | 455,520 MWh | [Model]
Site WUE annual | LBNL hyperscale 0.32–0.40; MSFT APAC 0.25 | 0.45 L/kWh | [Proxy: ~3,000–4,000 wet-mode hours]
Direct water | 350.4 M × 0.45 | 157,680 kL/yr (432 kL/d avg) | [Model]
Indirect water | 455.52 M × 2.8 | 1,275,456 kL/yr | [Model]
Total water | — | 1,433,136 kL/yr (source WUE 4.09) | [Model]
Peak day (Section 5.3) | 42 MW × Σ WUE | 906 kL/day (2.1× average) | [Model]
Peak hour | 42,000 × 1.60 | 67.2 kL/h (3.7× the 18 kL/h average hour) | [Model]
Storage | 24 h at peak-day rate | ~900 kL; 48 h ≈ 1,800 kL | [Model]
Contract demand | 50 × 1.45 = 72.5 MW ÷ 0.95 | ~76 MVA (220 kV) | [Model]
DG fuel | 72,500 × 0.26 | 18,850 L/h | [Model]
R12-T24 Example B: landed electricity cost by option
Source: Report 12 (Part 12 research report) · 8. Worked examples › Example B: 50 MW IT hyperscale, Hyderabad, air-side economiser / adiabatic-assisted cooling
Note: Landed electricity cost (455.5 MU; 76,000 kVA → demand ₹45.6 cr/yr = ₹1.00/kWh):
Data basis: Calculated (model output)
Used in atlas: Ch 12 cost-vs-water chart (Example B dots).
Used to derive: Cheapest procurement route.
Option | Calculation | ₹/kWh | Label
1. TGSPDCL HT-I(A) ≥132 kV + ToD | 6.65 + 1.00 demand − 0.17 ToD net (flat load: +1.00 × 8 h, −1.50 × 8 h) | 7.48 (₹340.7 cr) | [Model on TGERC rates]
1b. HT-II(A) commercial ≥132 kV | 7.80 + 1.00 − 0.17 | 8.63 | [Model]
2. HT-I + green tariff | 7.48 + 0.66 | 8.14 | [Model; TGERC Verified]
3. Group captive RE-RTC | 5.25 + ISTS/STU ~0.6 + wheeling ~0.4 [Proxy] + losses 0.3 + demand 1.00 (CSS/AS exempt) | 7.55 | [Model]
4. Third-party OA FDRE | 5.25 + 0.6 + 0.4 + CSS 1.46 (HT-I 132 kV) + AS ~0.5 [Proxy] + 0.3 + 1.00 | 9.51 | [Model; CSS Verified]
R12-T25 Example C: 100 MW Bengaluru AI campus, step by step
Source: Report 12 (Part 12 research report) · 8. Worked examples › Example C: 100 MW IT AI campus, Bengaluru (alt.: Visakhapatnam), direct-to-chip liquid cooling + dry coolers
Data basis: Calculated (model output)
Used in atlas: Ch 12 charts (Example C).
Used to derive: Water and cost for a Bengaluru AI campus.
Step | Calculation | Result | Label
Racks | 100,000 kW ÷ 120 kW (NVL72) | ~833 racks ≈ 60,000 GPUs | [Model; NVDA]
Average IT | 100 × 75% | 75 MW | [Proxy: LBNL training 80% × 70% rated, plus inference]
IT energy | 75 × 8,760 | 657,000 MWh | [Model]
PUE annual | Mild climate; ~80% heat to liquid at W32–W40 | 1.25 | [Proxy]
Facility energy | 657,000 × 1.25 | 821,250 MWh | [Model]
Site WUE | Closed loop; domestic + humidification | 0.03 L/kWh | [Proxy; Microsoft zero-water design Verified]
Direct water | 657 M × 0.03 | 19,710 kL/yr (54 kL/d) | [Model]
Indirect water | 821.25 M × 1.8 (Karnataka proxy) | 1,478,250 kL/yr | [Model]
Total water | — | 1,497,960 kL/yr (source WUE 2.28) | [Model]
With 90% RE-RTC | 821.25 M × 0.27 + 19.7 ML | ~241,400 kL/yr | [Model]
Peak water day | Domestic-driven; ~1.2× | ~65 kL/d (+ one-time loop fill) | [Model]
Hot-day electricity | April afternoon 34–35 °C → PUE 1.35 at 100 MW | 135 MW | [Model]
Contract demand | 135 ÷ 0.95 ≈ 142 → 150 MVA | 220/400 kV | [Model]
Load swings | Training square-wave drops | Specify BESS/UPS smoothing and ride-through | [Verified: LBNL24 Fig 3.4; NERC]
DG fuel | 135,000 × 0.26 | 35,100 L/h; 24 h ≈ 842 kL | [Model]
R12-T26 Example C: landed electricity cost by option
Source: Report 12 (Part 12 research report) · 8. Worked examples › Example C: 100 MW IT AI campus, Bengaluru (alt.: Visakhapatnam), direct-to-chip liquid cooling + dry coolers
Note: Landed electricity cost (821.25 MU; 150,000 kVA → demand ₹62.1 cr = ₹0.76/kWh):
Data basis: Calculated (model output)
Used in atlas: Ch 12 cost-vs-water chart (Example C dots).
Used to derive: Cheapest procurement route.
Option | Calculation | ₹/kWh | Label
1. KERC HT-2(a) via BESCOM | 6.60 + 0.76 demand + 0.36 P&G + 0.56 true-up | 8.28 (₹679.7 cr) | [Model on KERC rates; P&G/true-up applicability to HT Proxy]
2. Intra-state group captive (solar + wind + BESS) | 4.5–5.25 + wheeling/transmission 0.8–1.2 [Proxy] + banking 0.2 + demand 0.76 | 6.3–7.4 | [Model]
3. Third-party ISTS FDRE | 5.25 + ISTS 0.6–1.0 + CSS ~1.5 [Proxy] + AS 0–1.65 (BESCOM proposal; GEOA exempts if fixed charges paid) + wheeling 0.5 + 0.76 | 8.6–10.7 | [Model]
R12-T27 Bottom line across the three examples
Source: Report 12 (Part 12 research report) · 8. Worked examples › Example C: 100 MW IT AI campus, Bengaluru (alt.: Visakhapatnam), direct-to-chip liquid cooling + dry coolers
Data basis: Calculated (model output)
Used in atlas: Ch 12 "Where the water goes" chart.
Used to derive: Direct vs indirect water across examples.
Metric | A: Mumbai colo | B: Hyderabad hyperscale | C: Bengaluru AI
Direct water (ML/yr) | 245.3 | 157.7 | 19.7
Indirect water (ML/yr) | 551.9 | 1275.5 | 1478.3
Total (ML/yr) | 797.2 | 1433.1 | 1498
Direct L per facility kWh | 1.33 | 0.35 | 0.02
Cheapest modelled landed ₹/kWh | 7.94 (captive) | 7.48 (HT-I) | 6.3–7.4 (captive)
R12-T28 Data gaps and how to close them
Source: Report 12 (Part 12 research report) · Data gaps and how to close them
Data basis: Illustrative / framework / author judgement
Used in atlas: Data register "Data gaps" tab.
Used to derive: Next data to collect.
Gap | Request from | Instrument
Site WUE (withdrawal/consumption), source split, CoC | Nxtra, CtrlS, Yotta, Sify, STT GDC, AdaniConneX, NTT India | ESG/BRSR requests; Karnataka plant-wise PUE/WUE filings [Verified: KADC]
Water allocations and consents | State PCBs (CTE/CTO), MIDC, CMWSSB, HMWSSB, BWSSB, GVMC | RTI for CTO water quantities and STP/ZLD conditions
EIA water figures | MoEFCC PARIVESH | Portal downloads
CSS, AS, wheeling (MSEDCL, KERC); MSEDCL green tariff | MERC Tables 446–447; KERC tariff/OA orders | Regulator PDFs
Hourly DC load data | Grid-India / SLDCs, DISCOM AMR | Data-sharing MoU
Hourly climate | ISHRAE TMY for eight cities | Licence
Plant-level water intensity | CEA, plant CTO returns, WRI India | RTI; WRI satellite method
US/EU permit examples | The Dalles, Mesa, Goodyear/Quincy, Irish/Dutch permits | Follow-up research
Uptime Tier water/fuel autonomy text | Uptime Institute | Tier Standard: Topology

## Atlas R1-R9
Atlas-derived tables for Reports 1–9 (charts and calculators)
67 tables. Source line under each title; "Note" gives the context sentence from the report.
ATL-T01 Report 1: Five ways to classify a data centre
Source: Atlas Ch 1 (from Report 1)
Data basis: Illustrative / framework / author judgement
Used in atlas: Shown in atlas Ch 1 Types (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Axis | Question It Answers | Main Categories
Business model | Who owns and pays? | Enterprise, retail colo, wholesale colo, hyperscale, managed/cloud, edge
Workload | What runs inside? | General cloud, AI/HPC "AI factories", sovereign/government
Physical form | How is it built? | Traditional, modular/prefab, underground, underwater (experimental)
Reliability | How often can it fail? | Uptime Tier I–IV; ANSI/TIA-942 Rated 1–4
Cooling | How is heat removed? | Air, rear-door, direct-to-chip, immersion (see chapter 3)
ATL-T02 Report 1: Six data-centre business models
Source: Atlas Ch 1 (from Report 1); industry sources
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Shown in atlas Ch 1 Types (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Type | Size | How it works | Cost | Strengths | Weaknesses | Typical users | Direction
Enterprise on-prem | <1–20 MW | An organisation owns and runs its own facility, from a server room to a corporate campus. | All capex on the owner; low utilisation is common; modal rack ~7.5 kW. | Full control, data sovereignty, custom compliance. | Poor scale economics, older plant, hard to upgrade for AI. | Banks, government, defence, hospitals, manufacturers. | Share 56% (2018) → 32% (2026) → 19% (2031).
Retail colocation | 1 rack – 1 MW | Operator leases racks, cages or suites with power, cooling and security; the tenant brings servers. | Monthly rent per rack/kW plus cross-connects; India ~₹10,000–20,000 per kW-month all-in, 1.5–2.5× wholesale. | Capex becomes opex, carrier-neutral interconnection, fast. | Higher per-kW price, contract lock-in. | Enterprises, BFSI, networks, SaaS. | Where Indian banks move from captive rooms.
Wholesale colo / BTS | 10–100+ MW halls | Operator leases whole halls or buildings, often to one hyperscaler on a long lease. | Operator funds the build against an anchor lease; power passed through. India ~₹6,000–7,500/kW-month for 5 MW+. | Speed for hyperscalers, bankable cash flows; best risk-adjusted Indian return (~14–15%). | Tenant concentration, thin margins. | AWS, Microsoft, Google, Meta, AI labs. | Hyperscalers take 60–70% of new Indian colo demand.
Hyperscale self-build | 30 MW – 1 GW+ | Cloud giants design, own and operate their own campuses. | Balance-sheet capex; lowest unit cost; self-build ~13–27% cheaper than leasing in India. | Lowest cost per MW, custom hardware, best PUE (~1.44 for &gt;20 MW sites). | Concentrated power and water draw, local opposition, grid queues. | AWS, Microsoft, Google, Meta, Alibaba, Oracle. | 41% (2024) → 48% (2026) → ~67% (2031).
AI factory / GPU cloud | 50 MW – 5 GW | Facilities built around thousands of networked accelerators for training and inference. | IT dominates: ~₹266 cr/MW of GPUs on a ~₹72.5 cr/MW building. JLL sees 60% lease premiums. | Fast-growing demand; AI ~25% of workloads in 2025, ~50% by 2030 (JLL). | Hardware obsolescence, huge single-site power, utilisation risk. | Neoclouds, hyperscalers, IndiaAI empanelled providers. | IEA: accelerated server power grows ~30% a year.
Edge / micro | 50 kW – 5 MW | Small modular sites near users: telecom exchanges, towers, factories, cities. | Low capex per site, high cost per kW, many sites to run. | Low latency, data reduction, local resilience. | Hard to run at scale, uneven demand, little GPU density. | Telcos (5G), CDNs/OTT, payments, industrial IoT. Nxtra runs 120+ edge sites. | Real but small in MW; a complement, not a core.
ATL-T03 Report 1: Uptime Tier levels
Source: Atlas Ch 1 (from Report 1); Uptime Institute Tier Standard
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 1 Types (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Tier | Design availability | Downtime a year | Redundancy | Typical use
Tier I | 99.671% | 28.8 h | N, single path | Small business, dev/test
Tier II | 99.741% | 22 h | N+1 components, single path | Non-critical enterprise
Tier III | 99.982% | 1.6 h | N+1, concurrently maintainable | Colocation, cloud, banking production
Tier IV | 99.995% | 26 min | 2N, fault tolerant | Trading, critical health, national systems
ATL-T04 Report 1: Share of global data-centre capacity by owner type (%)
Source: Synergy Research Group (Apr 2026); 2031 is a projection
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 1 Types (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Year | Hyperscale | Colocation | Enterprise on-prem
2024 | 41 | 22 | 37
2025 | 44 | 22 | 34
2026 | 48 | 20 | 32
2031 (proj.) | 67 | 14 | 19
ATL-T05 Report 1: India capacity by city, H1 2026 (MW IT)
Source: Cushman & Wakefield India Data Centre H1 2026 Update
Note: City pipeline sums to 3,633 MW; C&W total is 3,860 MW (509 under construction, 3,351 planned).
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 1 Types (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
City | Operational (MW) | Pipeline to 2030 (MW)
Mumbai | 890 | 1726
Hyderabad | 151 | 710
Delhi NCR | 183 | 387
Chennai | 214 | 368
Pune | 133 | 258
Bengaluru | 162 | 100
Kolkata | 22 | 84
Total (7 markets) | 1789 | 3860
ATL-T06 Report 2: Global data-centre electricity (TWh)
Source: IEA, Energy and AI (Apr 2025), base case; 2035 extrapolated
Note: 2030 high case exceeds 1,260 TWh. IEA 2026 update: 485 → 950 TWh.
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Year | TWh
2024 | 415
2030 | 945
2035 | 1200
ATL-T07 Report 2: Share of facility electricity by use and facility class (%)
Source: Series synthesis from PUE ranges and IEA component shares (estimate)
Data basis: Proxy / estimate
Used in atlas: Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Facility class | IT | Cooling | Power losses | Lighting & other
Legacy (PUE ~1.9) | 52 | 35 | 10 | 3
Enterprise/colo (~1.55) | 64 | 27 | 7 | 2
Hyperscale (~1.15) | 88 | 7.5 | 3.5 | 1
AI liquid (~1.2) | 84 | 11 | 4.5 | 0.5
ATL-T08 Report 2: Rack power density by design (kW per rack)
Source: Nvidia specifications and GTC roadmap; industry estimates (Rubin)
Data basis: Proxy / estimate
Used in atlas: Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Design point | kW per rack
Enterprise modal | 8
Air practical limit | 20
Active RDHx | 60
GB200/GB300 NVL72 | 132
Vera Rubin | 210
Kyber (2027) | 600
ATL-T09 Report 2: Power-chain losses, grid to chip
Source: Atlas Ch 2 (Report 2); typical industry ranges
Data basis: Proxy / estimate
Used in atlas: Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Stage | Typical loss
Transformer | 1–2%
UPS | 2–8%
PDU / busway | 1–3%
Server PSU | 4–10%
ATL-T10 Report 2: Energy per workload
Source: Atlas Ch 2 (from Report 2)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Workload | Energy | Source
Google web search | ~0.3 Wh | Google, 2009 figure
Median Gemini text prompt | 0.24 Wh | Google, May 2025 (33× lower than a year earlier)
ChatGPT average query | ~0.34 Wh | Altman, June 2025
GPT-4o, 500 output tokens | ~0.3 Wh | Epoch AI
Long input, 10k / 100k tokens | 2.5 / 40 Wh | Epoch AI
Llama 3.1 405B training | ≤21.6 GWh | 30.84 M H100-hours (IT only, upper bound)
GPT-4 training (unofficial) | ~50–62 GWh | Estimates
ATL-T11 Report 2: Conventional vs AI data centre
Source: Atlas Ch 2 (from Report 2)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Attribute | Conventional | Ai Data Centre
Rack density | 5–15 kW (modal ~7–9) | 120–142 kW (GB200/GB300) → 190–230 kW (Rubin) → 600 kW+ (Kyber)
Cooling | Air, CRAH, containment | Direct-to-chip liquid mandatory; 85–100% of heat to liquid
Power | 400/415 V AC, 12 V boards | 415/480 V AC + 54 V busbars now; 800 V DC from 2027; site batteries
Networking | North–south, 10–100 GbE | East–west fabric, 400–800 Gb/s per GPU, many times more fibre
Campus size | 1–50 MW | 100 MW to multi-GW (Stargate Abilene ~1.2 GW, Meta Hyperion 2→5 GW)
Siting | Latency-first, near users | Power-first for training; metro for inference
Capex | JLL shell ≈US$11.3 m/MW; India ₹50–55 cr/MW | + up to US$25 m/MW fit-out before GPUs; India up to ₹75 cr/MW
Reliability | Tier III/IV, 2N | Training often N+1 (checkpoints); inference Tier III+
Obsolescence | Refresh every 5–7 years | New GPU generation yearly; economic life 3–6 years (contested)
ATL-T12 Report 2: Training vs inference sites
Source: Atlas Ch 2 (from Report 2)
Data basis: Illustrative / framework / author judgement
Used in atlas: Shown in atlas Ch 2 AI vs conventional (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Attribute | Training | Inference
Location | Power-rich, remote, cheap land | Metro or edge, near users
Size | 300 MW – 5 GW | 10–200 MW, distributed
Network | Huge internal fabric | Strong external peering
Redundancy | Lower (checkpointing) | Tier III+
Trend | Fewer, larger campuses | Most AI electricity by 2030
ATL-T13 Report 3: Heat a cubic metre of fluid carries per degree (kJ/m³·K)
Source: Standard physical properties
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Fluid | kJ/m³·K
Air | 1.2
Dielectric oil (1-phase) | 1750
Two-phase fluid (sensible) | 1850
PG25 coolant | 4000
Water | 4180
ATL-T14 Report 3: Heat-rejection options: water, energy and fit for India
Source: Atlas Ch 3 (from Report 3)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Heat Rejection | Wue L/Kwh | Energy | Fits India
Open cooling tower + water-cooled chiller | 1.4–2.5 | Lowest; cuts summer peak 25–35% | Only on recycled water
Adiabatic dry cooler | 0.1–0.5 | Moderate | Most Indian cities
Hybrid / thermosyphon | 0.5–0.7 | Near-evaporative | Mixed climates
Dry cooler + air-cooled chiller | ~0 | +5–15% (more in heat) | Water-stressed zones
DLC at W40–W45 + dry cooler | 0–0.1 | Small penalty | AI halls everywhere
Seawater heat exchange | ~0 fresh | Pumping only | Coastal (Vizag, Chennai, Mumbai)
ATL-T15 Report 3: Liquid cooling technologies compared
Source: Atlas Ch 3 (from Report 3); vendor-reported PUE
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Attribute | 1-Phase Dlc | 2-Phase Dlc | 1-Phase Immersion | 2-Phase Immersion
Rack density | 50–250 kW+ | 100–300 kW+ | 100–250 kW/tank | 200 kW+/tank
Heat to liquid | 70–98% | 70–95% | ~100% | ~100%
PUE (reported) | 1.05–1.20 | 1.04–1.15 | 1.03–1.08 | 1.01–1.05
Fluid | PG25/water | Dielectric refrigerant | Hydrocarbon oil | Fluorocarbon/HFO
Maturity 2026 | mainstream | early | niche | PFAS risk
ATL-T16 Report 3: Liquid-cooling manufacturer revenue (US$ bn)
Source: Dell'Oro Group (Jan 2026); 2029 projection
Note: India: US$113 m (2026) → US$790 m (2031), MarketsandMarkets.
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Year | US$ bn
2024 | 1.5
2025 | 3
2029 (proj.) | 7
ATL-T17 Report 3: Cooling-sector acquisitions 2024–26
Source: Company announcements
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Deal | Value
Eaton → Boyd Thermal | $9.5 bn
Ecolab → CoolIT | $4.75 bn
Vertiv → PurgeRite | ~$1 bn
Schneider → Motivair | $0.85 bn
Trane → LiquidStack | n/d
ATL-T18 Report 3: India HFC phase-down schedule (Kigali Amendment)
Source: Kigali Amendment to the Montreal Protocol (India, Group 2)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Milestone | Year / step
Baseline years | 2024–26
Freeze | 1 Jan 2028
−10% | 2032
−20% | 2037
−30% | 2042
−85% | 2047
ATL-T19 Report 3: City design temperatures used in the cooling chapter
Source: Atlas Ch 3 (from Report 3); indicative 0.4% summer conditions (estimate)
Data basis: Proxy / estimate
Used in atlas: Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
City | Design dry-bulb (°C) | Design wet-bulb (°C)
Bengaluru | 35 | 23
Hyderabad | 41 | 26
Pune | 39 | 25
Mumbai | 35 | 28
Chennai | 38 | 29
Visakhapatnam | 36 | 28
Delhi NCR | 45 | 29
ATL-T20 Report 3: What to use where in India
Source: Atlas Ch 3 (from Report 3)
Data basis: Illustrative / framework / author judgement
Used in atlas: Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Use Case | Inside The Room | Heat Rejection | Target
AI ≥40 kW/rack, any city | Single-phase DLC at W32–W45 + RDHx for residual | Dry coolers, adiabatic on peak days | PUE 1.15–1.25 · WUE <0.2
AI on the coast | DLC | Seawater or treated sewage water | PUE ~1.2 · freshwater ~0
Cloud 8–20 kW, Bengaluru/Hyderabad/Pune | Hot-aisle containment, fan walls | Indirect evaporative or free-cooling chillers | PUE 1.3–1.4
Cloud in Mumbai/Chennai | Containment, 18–20 °C chilled water | Magnetic-bearing chillers on recycled water | PUE 1.35–1.5
Edge, dusty sites | Sealed DX or immersion pods | Dry | —
ATL-T21 Report 3: Practical rack-density ceiling by cooling method (kW)
Source: Atlas Ch 3 cooling selector (estimate)
Data basis: Proxy / estimate
Used in atlas: Shown in atlas Ch 3 Cooling (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Method | kW per rack
Perimeter air (CRAH) | 15
Air + containment | 30
Active rear-door HX | 70
Direct-to-chip liquid | 250
Immersion | 250
ATL-T22 Report 4: Bengaluru's water sources
Source: Atlas Ch 4 (from Report 4); BWSSB, Karnataka groundwater assessment
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Source | Status
Cauvery (BWSSB) | ~1,935 MLD delivered of 2,225 MLD capacity; Stage V supplying ~485 of 775 MLD; industrial tariff ₹99/kL
Groundwater | 1,457 MLD extracted in 2024 (from 600 in 2020); every taluk over-exploited; Bangalore East ~305%, Devanahalli 169%
Tankers | Mostly peri-urban borewell water; prices spike March–May
Treated wastewater | ~1,348.5 MLD STP capacity; only ~30 MLD reused commercially; ₹10–20/kL
ATL-T23 Report 4: Grid connection by contract demand (Karnataka)
Source: KERC conditions of supply (as reported)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Contract Demand | Voltage | Fits
Up to 20 MVA | 66 kV | Small colo
Up to 35 MVA (55 MVA since June 2025, if feasible) | 110 kV | 20 MW colo (~35 MVA)
Above 20 MVA | 220 kV, dual circuit | 50–100 MW (80–140 MVA)
300 MW+ campuses | 400 kV | Multi-phase AI parks
ATL-T24 Report 4: Water use compared with other users (MLD)
Source: Atlas Ch 4 (from Report 4)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
User | MLD
JSW Vijayanagar (allocation) | 330
Raichur TPS (1,720 MW) | ~130
IT campus, 10 m sq ft | ~6
Toyota Bidadi | 4.7
Brewery, 2 m hl/yr | 1.7
50 MW DC, evaporative | 1.47
20 MW colo, evaporative | 0.62
1,000-flat apartments | 0.61
500-bed hospital | 0.23
100 MW AI, DLC + dry | 0.13
ATL-T25 Report 4: Bengaluru data centres' water use today: estimates (MLD)
Source: Down To Earth; Karnataka IT dept; series model; WELL Labs
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Estimate | MLD
DTE: permitted volumes | ~2.2
Karnataka IT dept (32 DCs) | ~4
Series model, mixed cooling | 4–5
Series model, all evaporative | ~8.8
WELL Labs heuristic | ~20
ATL-T26 Report 4: Scaling to Karnataka's 1 GW target: on-site water by cooling choice (MLD)
Source: Report 4 model, 75% utilisation
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Added capacity | Evaporative (WUE 1.8) | Adiabatic (0.4) | Dry / DLC (0.05) | Power-station water
+100 MW | 3.2 | 0.7 | 0.09 | 3.5
+500 MW | 16.2 | 3.6 | 0.45 | 17.6
+1 GW | 32.4 | 7.2 | 0.9 | 35.1
ATL-T27 Report 4: Bengaluru campus central cases
Source: Report 4 model
Note: Only the values shown in the atlas are listed; dashes are not given there.
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Case | IT MW | Utilisation | PUE | WUE (L/kWh) | Facility energy (MU/yr) | Contract demand | On-site water (MLD)
20 MW colo, air | 20 | 70% | 1.45 | 1.8 | 177.8 | ~33 MVA, 110 kV | 0.6
50 MW hyperscale, evaporative | 50 | — | — | — | — | 80–140 MVA band | 1.47
100 MW AI, liquid + dry | 100 | — | — | — | ~841 | ~140 MVA, 220 kV | 0.13
ATL-T28 Report 4: Recommended Karnataka roadmap
Source: Atlas Ch 4 (from Report 4)
Data basis: Illustrative / framework / author judgement
Used in atlas: Shown in atlas Ch 4 Bengaluru (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Phase | When | Actions
1 | Q4 2026–2027 | Operational guidelines; mandatory metering and disclosure; ban groundwater for cooling in over-exploited taluks; data-centre water tariff (₹150–200/kL potable); publish grid hosting-capacity map
2 | 2027–2028 | WUE ≤0.4 and PUE ≤1.3 in consents for new builds; treated-water pipelines to Hoskote and Whitefield; ≥70% renewable rule above 50 MW; batteries and demand response
3 | 2029–2031 | Existing fleet to WUE ≤1.0 and PUE ≤1.45; hourly renewable matching; independent audits; review the 1 GW target
ATL-T29 Report 5: Carbon of 1 TWh of data-centre load, by supply (Mt CO₂)
Source: Report 5 comparison (CEA, Ember, IPCC)
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Supply | Mt CO₂ per TWh
India grid avg (+8% losses) | 0.77
Karnataka mix | 0.54
Marginal coal, evening peak | 1.09
24/7 RE + battery (90% CFE) | 0.11
France (nuclear) | 0.045
Norway (hydro) | 0.025
Nuclear with towers | 0.009
Gas CCGT | 0.49
ATL-T30 Report 5: Karnataka illustrative hourly grid intensity, dry season (gCO₂/kWh)
Source: Modelled from a third-party dashboard; no official hourly factor exists
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Hour | Average intensity | Marginal unit (coal)
0 | 580 | 980
1 | 580 | 980
2 | 575 | 980
3 | 575 | 980
4 | 570 | 980
5 | 565 | 980
6 | 560 | 980
7 | 500 | 980
8 | 420 | 980
9 | 330 | 980
10 | 270 | 980
11 | 240 | 980
12 | 220 | 980
13 | 215 | 980
14 | 225 | 980
15 | 260 | 980
16 | 330 | 980
17 | 430 | 980
18 | 540 | 1080
19 | 600 | 1080
20 | 610 | 1080
21 | 600 | 1080
22 | 590 | 1080
23 | 585 | 980
ATL-T31 Report 5: Lifecycle carbon by source (gCO₂e/kWh)
Source: IPCC AR5 Annex III medians
Note: Indian coal units actually run at 900–1,100 g; CEA grid average 710 g (FY25).
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Source | gCO₂e/kWh
Coal | 820
Gas CCGT | 490
Solar PV | 48
Hydro | 24
Nuclear | 12
Wind | 11
ATL-T32 Report 5: Water consumed by generation source (L/MWh)
Source: CSE, NREL, CEA research
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Source | L/MWh
Coal, tower (India actual) | ~3,400
CSP, wet tower | ~3,250
Nuclear, tower | ~2,600
Gas CCGT, tower | ~850
Solar PV (cleaning) | 20–100
Wind | ~0
ATL-T33 Report 5: Microsoft Scope 2 emissions (Mt CO₂e)
Source: Microsoft sustainability reports
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Year | Location-based | Market-based
FY20 | 4.33 | 0.456
FY24 | 9.96 | 0.259
ATL-T34 Report 5: Carbon per IT-kWh, worked (CUE = PUE × grid factor)
Source: Atlas Ch 5 (from Report 5)
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Case | Kgco₂/It-Kwh
PUE 1.5 on Indian grid (0.77 at meter) | 1.16
PUE 1.5 on Karnataka mix (0.50) | 0.75
PUE 1.5 with 90% hourly clean energy | 0.17
Same compute in France | ~0.05–0.09
ATL-T35 Report 5: Five-factor scorecard weights
Source: Report 5 framework
Data basis: Illustrative / framework / author judgement
Used in atlas: Shown in atlas Ch 5 Carbon (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Factor | Weight
Carbon | 30%
Water | 25%
Source | 20%
Timing | 15%
Location | 10%
ATL-T36 Report 6: Monthly withdrawal, 50 MW evaporative site (MLD)
Source: Report 6 model
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Month | Withdrawal (MLD)
Jan | 1.5
Feb | 1.68
Mar | 2.04
Apr | 2.3
May | 2.3
Jun | 1.77
Jul | 1.59
Aug | 1.59
Sep | 1.68
Oct | 1.68
Nov | 1.5
Dec | 1.5
ATL-T37 Report 6: Scarcity-weighted water footprint, 50 MW (Mm³-eq/yr)
Source: Report 6 model; illustrative AWARE-style weights
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Scenario | On site | Off site (power plants)
A · Evap, East groundwater | 50.9 | 34.2
B · Evap, potable | 30.5 | 34.2
C · Evap, treated + RO | 15.3 | 34.2
D · Dry + grid | 1.1 | 38.1
E · Dry + renewable PPA | 1.1 | 2.5
ATL-T38 Report 6: Water per AI prompt, by boundary (mL)
Source: Google; Li et al.; Mistral LCA; Report 6 model
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Case | mL
Bengaluru DLC, site only | 0.03
Google Gemini, on-site | 0.26
Bengaluru DLC, site + grid | 0.5–0.9
Same site on coal power | ~2
GPT-3, India case (UCR) | 19.7
Mistral Large 2, full LCA | 45
ATL-T39 Report 6: Impact scorecard
Source: Atlas Ch 6 (from Report 6)
Data basis: Illustrative / framework / author judgement
Used in atlas: Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Scenario | Score | Decision
A · Evaporative, Bangalore East groundwater | 4.6 | Refuse
B · Evaporative, BWSSB potable | 4 | Redesign
C · Evaporative, treated water + RO | 3.8 | Conditional
F · 100 MW AI, DLC on treated water | 3.3 | Conditional
D · Dry cooling | 2.6 | Acceptable
E · Dry + renewable PPA | 1.9 | Preferred
ATL-T40 Report 6: Bengaluru scenarios: site and source water
Source: Atlas Ch 6 (from Report 6) model
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Bengaluru Scenario | Site Wue | Source Wue | L Per H100-Hour (Site/Total) | Ml Per Prompt (Site/Total)
S1 · 20 MW colo, evaporative | 1.8 | 3.9 | 1.8 / 3.9 | 0.39 / 0.84
S2 · 50 MW hyperscale, evaporative CoC 5 | 1.85 | 3.8 | 1.85 / 3.8 | 0.43 / 0.88
S3 · 50 MW dry | 0.05 | 2.23 | 0.05 / 2.2 | 0.01 / 0.46
S4 · 100 MW AI, DLC + adiabatic | 0.13 | 1.86 | 0.13 / 1.9 | 0.03 / 0.48
ATL-T41 Report 6: Suggested water thresholds
Source: Atlas Ch 6 (from Report 6) (proposal)
Data basis: Illustrative / framework / author judgement
Used in atlas: Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Indicator | Green | Amber | Red
Site consumption WUE (L/kWh) | ≤0.2 | 0.2–1.0 | >1.0
Groundwater for cooling, over-exploited taluk | 0% | — | >0%
Withdrawal ÷ taluk recharge | <0.5% | 0.5–1% | >1%
Peak ÷ average without curtailment plan | <1.5 | 1.5–3 | >3
Source WUE (L/kWh) | <1.0 | 1.0–2.5 | >2.5
ATL-T42 Report 6: Cooling-tower water balance, 50 MW (default CoC 5)
Source: Report 6 model
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 6 Water impact (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Item | Value
IT energy | 350.4 GWh/yr (50 MW × 80%)
Evaporation | 504.6 ML/yr
Drift | 1.2 ML/yr
Non-cooling use | 14.6 ML/yr (80% returned)
Withdrawal | 646.6 ML/yr (1.77 MLD)
Consumption | 508.7 ML/yr (1.39 MLD)
Withdrawal WUE | 1.85 L/kWh
Consumption WUE | 1.45 L/kWh
RO recovery | 75%
ATL-T43 Report 7: Data-centre construction cost by market (US$/W)
Source: Turner & Townsend Data Centre Cost Index 2025
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Market | US$/W
Tokyo | 15.2
Singapore | 14.5
Zurich | 14.2
Silicon Valley | 13.3
New Jersey | 12.9
Oslo | 12.4
London | 12
Frankfurt | 11.6
Atlanta | 9.9
Phoenix | 9.8
Charlotte | 9.5
Mumbai | 6.64
ATL-T44 Report 7: Capex per MW by category, three cases (₹ crore/MW)
Source: Report 7 model
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Case | Land | Shell & core | Electrical | Cooling | Backup | Fire, BMS, network | Soft, contingency, IDC
A · 20 MW colo | 5 | 8.5 | 22 | 10 | 4.2 | 3 | 8.4
B · 50 MW hyperscale | 3.2 | 5.5 | 15.5 | 7.5 | 3.3 | 1.7 | 5.7
C · 100 MW AI | 1.5 | 7 | 28 | 17 | 6 | 3 | 11.5
ATL-T45 Report 7: Capex line by line: A · 20 MW Tier III colo
Source: Report 7 model
Note: ₹56.1 cr/MW = US$6.2/W, consistent with Turner & Townsend Mumbai (US$6.64/W) and SBI (₹50–55 cr/MW before soft costs).
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Item | ₹ cr/MW | ₹ crore | Share
Land (0.25 acre/MW at ₹20 cr/acre) | 5 | 100 | —
Shell & core, civil/structural | 8.5 | 170 | 15.2%
Electrical (substation, transformers, switchgear, 2N UPS, PDUs, busway) | 22 | 440 | 39.2%
Cooling (chillers, towers/adiabatic, CRAH, piping) | 10 | 200 | 17.8%
Backup (DG N+1 ~42 MVA, fuel) | 4.2 | 84 | 7.5%
Fire, BMS/DCIM, security | 2 | 40 | 3.6%
Networking (meet-me rooms, fibre) | 1 | 20 | 1.8%
Design, permits, PMC | 3 | 60 | 5.3%
Contingency | 2.5 | 50 | 4.5%
Interest during construction | 2.9 | 58 | 5.2%
Facility total (excl. land) | 56.1 | 1122
Total incl. land | 61.1 | 1222
ATL-T46 Report 7: Capex line by line: B · 50 MW hyperscale BTS
Source: Report 7 model
Note: A powered-shell-only variant (building, substation, utility yard) costs ~₹12–15 cr/MW, with returns closer to industrial real estate.
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Item | ₹ cr/MW | ₹ crore | Share
Land (0.4 acre/MW at ₹8 cr/acre) | 3.2 | 160 | —
Shell & core | 5.5 | 275 | 14.0%
Electrical (incl. 220 kV substation) | 15.5 | 775 | 39.5%
Cooling | 7.5 | 375 | 19.1%
Backup (DG) | 3.3 | 165 | 8.4%
Fire, BMS, security | 1.4 | 70 | 3.6%
Networking / meet-me rooms | 0.3 | 15 | 0.8%
Soft costs | 1.7 | 85 | 4.3%
Contingency | 1.7 | 85 | 4.3%
Interest during construction | 2.3 | 115 | 5.9%
Facility total | 39.2 | 1960
Total incl. land | 42.4 | 2120
ATL-T47 Report 7: Capex line by line: C · 100 MW AI campus
Source: Report 7 model
Note: IT is 3.7× the facility. At the US$6.0–6.5 m GB300 price some sources quote, the campus would cost ~₹45,000 crore.
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Item | ₹ cr/MW | ₹ crore | Share
Land (0.3 acre/MW at ₹5 cr/acre) | 1.5 | 150 | —
Shell & core | 7 | 700 | 9.7%
Electrical (400/220 kV, busway, UPS) | 28 | 2800 | 38.6%
Cooling (CDUs, DLC loops, dry coolers, trim chillers) | 17 | 1700 | 23.4%
Backup (DG N+1 + BESS) | 6 | 600 | 8.3%
Fire, BMS | 2 | 200 | 2.8%
Network infrastructure | 1 | 100 | 1.4%
Soft / contingency / IDC | 11.5 | 1150 | 15.8%
GPU racks: ~590 × GB300 NVL72 at ~US$4.2 m | 223 | 22300 | IT
Back-end fabric (~12% of cluster) | 32 | 3240 | IT
Storage, front-end, CPU, management | 11 | 1080 | IT
Facility total (excl. land) | 72.5 | 7250
Campus total incl. 42,480 GPUs | 340 | 34020
ATL-T48 Report 7: Colocation opex, Case A (₹ crore a year)
Source: Report 7 model
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Item | ₹ crore/yr
Electricity | 129
Maintenance (AMC) | 15.3
SG&A | 15
Personnel | 7.5
Insurance | 2.2
DG fuel & testing | 1.5
Property tax | 1.5
Network | 1
Water & chemicals | 1
ATL-T49 Report 7: What moves the colo LCOD (₹ per IT-kWh; base 29.7)
Source: Report 7 model
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Lever | Better case | Worse case
Utilisation (full vs 70% billed) | 22 | 35
Capex ±10% | 28.3 | 31.1
PUE 1.35 / 1.65 | 28.5 | 30.9
Tariff ±₹1/kWh | 28.2 | 31.2
WACC 10% / 12% | 28.8 | 30.6
ATL-T50 Report 7: GPU-hour market prices, H100-class (Oct 2026)
Source: IndiaAI; provider price pages; OCPI index
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Offer | ₹/Gpu-Hr
IndiaAI L1 rate (users pay ~₹92 after subsidy) | 150
JarvisLabs H100 | 218
Global OCPI-H100 index (US$2.79) | ~251
E2E Networks on-demand | 255.55
Yotta Shakti dedicated / on-demand | ~269 / 356
Hyperscaler on-demand (US$6–12) | 540–1,080
ATL-T51 Report 7: Returns by business model
Source: Report 7 model
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Metric | Colo (A) | Hyperscale (B) | Ai Neocloud (C)
Capex/MW | ₹61 cr | ₹42 cr | ₹340 cr
EBITDA margin | 42% | 84% of rent | 90%
Payback | 9.6 yrs | 7.1 yrs | 3.2 yrs
Unlevered IRR | ~9.5% | ~14.7% | 21.5% → negative
Power share of cost | 39% | 48% | ~6%
ATL-T52 Report 7: India vs US vs Singapore
Source: C&W, CBRE, JLL, Turner & Townsend
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Metric | India | US | Singapore
Build (US$/W) | 6.64 | 9.5–13.3 | 14.5
Rent (US$/kW/mo) | 80–100 | 160–225 | 300–475
Electricity (US$ m/MW/yr) | 0.7–0.9 | ~1.22 | ~1.7
Cap rate | 7.5–8.5% | 4.5–6.5% | 5.0–6.5%
ATL-T53 Report 7: Land and power by hub
Source: Market reports; state tariff orders
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Hub | ₹ Cr/Acre | Ht Energy ₹/Kwh
Navi Mumbai | 15–40 (in-fill ~80) | 7.27 (MH)
Chennai Ambattur / Oragadam | 8–15 / 3–8 | 7.50 (TN)
Hyderabad | 2–6 | 6.65 at 132 kV
Bengaluru Devanahalli/Hoskote | 4–10 (est.) | ~6.70 (KA)
RTC renewable (SECI tranche V) | — | 5.25–5.26 at bus
ATL-T54 Report 7: GPU cost model inputs
Source: Report 7 assumptions
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 7 Unit economics (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Input | Value
H100 HGX (8 GPUs) | ~US$275k
H200 HGX (8 GPUs) | ~US$315k
B200 HGX (8 GPUs) | ~US$450k
kW per GPU incl. server share | H100/H200 1.4; B200 2.0
PUE | 1.35 (1.30 for B200)
Colo hosting | ₹7,000 per kW-month
Support, software, spares | ₹70,000 a year
Economic life | 5 years
WACC | 11%
Result: H100 at 80% use | ~₹178 per GPU-hour
ATL-T55 Report 8: Abatement cost by measure, 20 MW Bengaluru colo (₹/tCO₂)
Source: Report 8 model
Note: India carbon credit price expected ~₹955/t initially; EU ETS ~€84/t.
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 8 Green (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Measure | ₹ per tCO₂
Efficiency + water | -8450
RE at ₹0.75 discount | -1060
Full package | -2540
RE at ₹0.50 premium | 700
ATL-T56 Report 8: PUE thresholds around the world
Source: EU, Germany EnEfG, Karnataka, China, Singapore IMDA, MeitY, Uptime
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 8 Green (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Threshold | PUE
EU grade A | 1.15
Germany, new (2026) | 1.2
Karnataka incentive | 1.2
China hubs | 1.2
Singapore 2026 | 1.25
China large DCs | 1.25
CNDCP warm climate | 1.4
MeitY AI tender | 1.35
Indian leaders today | 1.45
Global average | 1.54
ATL-T57 Report 8: Green upgrade case, 20 MW Bengaluru colo
Source: Report 8 model
Data basis: Calculated (model output)
Used in atlas: Shown in atlas Ch 8 Green (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Item | Value
IT capacity / load | 20 MW / 70%
PUE | 1.50 → 1.25
Hourly renewable share | 80%
Grid tariff / RE landed cost | ₹8.00 / ₹7.25 per kWh
Green capex premium | ₹60 crore
Savings a year | ₹35.5 crore (efficiency 24.5, renewables 9.2)
Payback (efficiency + water) | 2.3 years
CO₂ avoided | ~108,843 t a year (83%)
Freshwater saved | ~196 ML a year
Abatement cost | −₹2,536 per tCO₂
ATL-T58 Report 8: Twelve dimensions of a green data centre
Source: Report 8 framework
Data basis: Illustrative / framework / author judgement
Used in atlas: Shown in atlas Ch 8 Green (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
# | Dimension | Metric | India target
1 | Energy efficiency | PUE | ≤1.30 air; ≤1.20 liquid AI
2 | Carbon-free energy | Hourly CFE, CUE | ≥70–80% hourly; CUE ≤0.3
3 | Water | Freshwater WUE | ≤0.2 L/kWh; treated water for any trim
4 | Embodied carbon | kgCO₂e per MW | 30–40% below baseline
5 | IT hardware (Scope 3) | PCF per server/GPU | Supplier footprints; longer refresh
6 | Circularity | % assets reused | ≥90% via authorised e-waste channels
7 | Heat reuse | ERF | Heat-reuse ready; absorption cooling
8 | Refrigerants | GWP, leakage | Low-GWP or chiller-less
9 | Land & biodiversity | Footprint | Brownfield / park siting
10 | Backup power | Diesel run-hours | HVO-ready, BESS for short events
11 | Grid-friendliness | Flexible MW | BESS services; schedulable training
12 | Social licence | Public disclosure | Site dashboards, water commitments
ATL-T59 Report 8: Spotting greenwashing
Source: Atlas Ch 8 (from Report 8)
Data basis: Illustrative / framework / author judgement
Used in atlas: Shown in atlas Ch 8 Green (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Claim | Credible If… | Red Flag
"100% renewable" | Hourly matching, same grid, new capacity, location-based also shown | Annual unbundled RECs from old hydro
"Carbon neutral" | Deep cuts first, removals for residuals | Cheap avoidance offsets
"PUE 1.2" | Annualised, measured at the utility meter, real load | Design PUE at full load, one cool month
"Water positive" | Site WUE disclosed; replenishment in the same basin | Credits elsewhere while drawing borewells
"Green certified" | Operational certification on measured data | Design-stage label never re-checked
ATL-T60 Report 8: Buying clean power in India
Source: Atlas Ch 8 (from Report 8); SECI; KERC
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 8 Green (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Route | Landed ₹/Kwh | Catch
Rooftop solar | 3–4 | <2–5% of a DC's load
Group captive (≥26% equity) | 5.5–7 | Avoids CSS and additional surcharge
Third-party open access | 6.5–8 | Surcharges, banking limits
ISTS hybrid PPA | 5–6.5 + charges | Better hourly profile
SECI RTC/FDRE | ~5.25 + delivery | High CFE share
Unbundled RECs | +0.1–0.3 | Weakest claim
ATL-T61 Report 8: Green rules elsewhere
Source: EU, Germany, Singapore, China, India
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 8 Green (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Jurisdiction | Key Requirement
Germany (EnEfG) | New sites PUE ≤1.2 from July 2026; 100% renewable from 2027; heat reuse 10→20%
European Union | A–G grades for every site >500 kW from Aug 2027 (A: PUE ≤1.15, WUE ≤0.10)
Singapore | 2026 round: PUE 1.25 at full load, ≥50% green energy, Green Mark Platinum
China | New large DCs PUE ≤1.25 (≤1.2 in hubs); ≥80% renewable in hubs
India | No binding national threshold; MeitY tenders PUE <1.35; Karnataka PUE/WUE reporting
ATL-T62 Report 8: Indian operators' green disclosures
Source: Company reports
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 8 Green (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Operator | Latest Disclosed
Nxtra (Airtel) | 49% RE in core DCs (FY25), first Indian DC in RE100, 70% target
AdaniConneX | US$875 m sustainability-linked loan, KPIs on efficiency and RE
Sify | >231 MW RE contracted; limited PUE disclosure
CtrlS | Captive solar for Mumbai; NTPC Green partnership
Yotta | Green tariff via TUCO (hydro, biogas)
ATL-T63 Report 9: State data-centre policy register
Source: State policy documents and GRs (Report 9)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 9 State policies (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
State | Status | Instrument | Power incentives | Green conditions | Target | Land & approvals | Projects | Assessment
Maharashtra | active | IT/ITeS 2023 + Green DC Parks GRs (Oct 2024, Jun 2026) | ED waiver 20 yrs; ₹1/unit for 10–20 yrs | 51% RE (cut from 100%) | 20 parks; 30–40 GW by 2047 | 100% stamp duty (parks); DCs allowed in any zone; extra FSI | Mumbai ~890 MW live; Lodha Palava park MoU (secondary). | Strongest ecosystem: subsea cables, exchanges, tenants. Green floor weakened in June 2026; water rules not codified.
Telangana | legacy | Data Centres Policy 2016 + bespoke packages | Power incentives; dual grid; essential service | None | ~5 GW by 2029–30 (stated) | Govt land subsidy; 50% building-fee rebate | Hyderabad 151 MW live; AWS ₹60,000 cr; TCS HyperVault up to 1 GW; CtrlS 400 MW; NTT–Neysa 400 MW. | Inland, low seismic risk, hyperscaler-anchored. Runs on a ten-year-old policy and opaque deals with no water or efficiency rules.
Andhra Pradesh | active | DC Policy 4.0, G.O.Ms.No.6 (14.11.2024) | Industrial tariff; T&W case-by-case | Seawater cooling; "70% RE" stated, not notified | 200 MW–1 GW in policy; 6.5 GW claimed | 100% stamp duty first sale; land discounts for mega projects (>50 MW or >₹5,000 cr) | Google US$15 bn (~1 GW, Vizag), Reliance 1 GW, Meta–Sify 500 MW. | Most generous and fastest for anchors. Opaque bespoke packages now face PILs on water, wildlife and Dalit land.
Tamil Nadu | lapsed | DC Policy 2021 (lapsed 31.3.2026) | 100% electricity tax subsidy, 5 yrs | ≥30% RE for eligibility | — | 50–100% stamp duty; 50% land subsidy (Cat C); FSI and zoning relaxations | Chennai 214 MW live; MoUs with Adani, L&T, STT GDC, CtrlS, Nxtra. | Chennai has top subsea connectivity, but no successor policy has been notified since the lapse.
Uttar Pradesh | active | DC Policy 2026 (replaced 2021) | ED waiver 10 yrs; T&W relief; dual grid | PUE/green-cert booster; 50% RE by 2030 | +2 GW; ₹2 lakh cr | 25–50% land subsidy; 100% stamp duty | 644 MW proposed under 2021 policy, ~101 MW commercialised; Yotta, NTT, STT, AdaniConneX, CtrlS. | Most transparent state and first with AI-compute incentives. Regional land subsidy drew no projects outside Noida.
Gujarat | active | DC Policy 2026–29 + IT/ITeS 2022–27 | ₹1/unit for 20 yrs; ED reimbursement 20 yrs | 51% RE for incentives | 7.5 GW; ₹6 lakh cr | 100% stamp duty and registration; cap 75% of fixed capital over 20 yrs | L&T Vyoma 250 MW at Dholera; GIFT City IFSC benefits. | Renewable land and cheap solar, but few subsea landings and no water plan for drought-prone areas.
Karnataka | active | Sustainable DC Policy 2026–31 (Sept 2026) | ED exemption; wheeling reimbursement | PUE/WUE reporting; ₹20 cr for PUE ≤1.20; WUE and treated-water reimbursement | 1 GW by 2031; ₹1,300.45 cr outlay | Parks at Hoskote, Mangaluru, Mysuru on 30+30-yr leases | 32 DCs, Bengaluru 162 MW live; Hoskote ~500 MW park with 60 MLD treated water planned. | India's best sustainability design, but incentives are small for hyperscale and Bengaluru has grid and water limits.
Haryana | active | State Data Centre Policy 2022 | ED waiver 20 yrs; power bill ≤25% of SGST | None | 115–120 DCs; ₹7,500 cr | 100% stamp duty; FAR relaxation; essential service (ESMA) | Gurugram cluster serving NCR. | Solid incentives next to Delhi demand; expensive Gurugram land and no green provisions.
West Bengal | expiring | DC Policy 2021, No. 490-ITE (lapses ~Sept 2026) | ED waiver 5 yrs; dual grid | Captive water treatment | 400 MW by 2025 (missed) | 100% stamp duty and registration; edge DC support | Kolkata ~67 MW; Adani 51.8 acres, Jio 40 acres at New Town. | Only eastern hub with a dedicated policy; about to lapse.
Odisha | active | State Data Centre Policy 2022 | 30% power-bill subsidy 5 yrs; ED 10 yrs; captive-RE T&W 100% | Clean-green subsidy; carbon framing | — | IDCO land at concessional rates; stamp duty 100/50% | Few projects so far. | Strong incentives and water security on paper; little track record.
Rajasthan | active | Data Centre Policy 2025 | Banking/T&W 100% waiver; ED 7 yrs | ZLD, recycling, green buildings; green incentive ≤₹12.5 cr | 300 MW; ₹20,000 cr | Stamp duty and conversion exemptions | Early stage. | Best renewables and a model water framework; far from connectivity and demand.
Madhya Pradesh | active | IT/ITeS & ESDM Policy 2023 | Tariff rebate; ED waiver | Vague green support | — | 25% capex up to ₹125 cr for first 5 anchors | CtrlS Bhopal (₹500 cr); RackBank Indore. | Generous anchor subsidy; limited connectivity.
Bihar | active | IT Policy 2024 | 25% tariff subsidy 5 yrs | None | — | 30% capex up to ₹30 cr or interest subvention | None identified. | Data centres covered as an ancillary sector.
Chhattisgarh | active | Industrial Development Policy 2024–30 | Not verified | None | — | SEZ route available | RackBank AI park, Nava Raipur (5 → 150 MW). | Data-centre clauses not verified.
Punjab | active | Industrial & Business Dev. Policy 2022 | ED exemption | None | — | 100% stamp duty; CLU/EDC exemption | None identified. | IT-unit benefits apply to data centres.
ATL-T64 Report 9: State attractiveness factor scores (0–10) and index
Source: Report 9 judgement; index uses report weights 25/15/15/15/10/10/10
Data basis: Illustrative / framework / author judgement
Used in atlas: Shown in atlas Ch 9 State policies (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
State | Power | Renewables | Connectivity | Incentives | Land | Water | Regulatory | Index | Sustainability rank
Maharashtra | 8 | 6 | 10 | 8 | 6 | 6 | 8 | 7.6 | 8
Telangana | 8 | 7 | 6 | 7 | 9 | 6 | 7 | 7.2 | —
Andhra Pradesh | 7 | 9 | 7 | 9 | 7 | 5 | 6 | 7.3 | 4
Tamil Nadu | 7 | 8 | 10 | 4 | 6 | 4 | 5 | 6.55 | 7
Uttar Pradesh | 7 | 5 | 6 | 8 | 7 | 6 | 8 | 6.7 | 3
Gujarat | 7 | 9 | 4 | 9 | 8 | 4 | 7 | 6.95 | 5
Karnataka | 6 | 8 | 5 | 6 | 6 | 4 | 7 | 6.05 | 1
Haryana | 6 | 4 | 6 | 7 | 4 | 4 | 7 | 5.55 | —
West Bengal | 6 | 4 | 6 | 5 | 6 | 7 | 4 | 5.45 | —
Odisha | 7 | 6 | 4 | 7 | 7 | 7 | 6 | 6.3 | 6
Rajasthan | 6 | 10 | 2 | 8 | 8 | 2 | 6 | 6.1 | 2
Madhya Pradesh | 6 | 6 | 3 | 7 | 7 | 5 | 6 | 5.7 | —
ATL-T65 Report 9: Policy validity periods
Source: State policies (Report 9)
Note: Years are decimal (e.g. 2026.25 = end of March 2026).
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 9 State policies (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Instrument | Start (year) | End (year) | Status
Telangana 2016 | 2016.2 | 2027 | legacy
Tamil Nadu 2021 | 2021.9 | 2026.25 | lapsed
West Bengal 2021 | 2021.7 | 2026.7 | expiring
UP 2021 | 2021.1 | 2026.07 | lapsed
Haryana 2022 | 2022.5 | 2029.5 | active
Odisha 2022 | 2022.5 | 2027.5 | active
Maharashtra IT 2023 | 2023.3 | 2028.3 | active
MP IT 2023 | 2023.5 | 2028.5 | active
AP 4.0 | 2024.87 | 2029.87 | active
Rajasthan 2025 | 2025.1 | 2030.1 | active
Gujarat DC 2026 | 2026.5 | 2029.5 | active
UP 2026 | 2026.5 | 2031.5 | active
Karnataka 2026 | 2026.7 | 2031.7 | active
ATL-T66 Report 9: Electricity-duty holiday by state (years)
Source: State policies
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 9 State policies (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
State (policy) | Years
Tamil Nadu (2021) | 5
West Bengal (2021) | 5
Rajasthan (2025) | 7
Uttar Pradesh | 10
Odisha (2022) | 10
Haryana (2022) | 20
Maharashtra (2026) | 20
Gujarat (2026) | 20
ATL-T67 Report 9: The central framework
Source: Atlas Ch 9 (from Report 9)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Shown in atlas Ch 9 State policies (chart, table or calculator data built from the report).
Used to derive: Same purpose as the matching report table; restated in the form the atlas displays.
Instrument | Status · Effect
Draft National DC Policy (2020) | Never notified; consultations revived
Infrastructure status (Oct 2022) | DCs ≥5 MW; long-tenor debt, ECBs
Budget 2026–27 | Tax holiday to 31 Mar 2047 for foreign cloud firms using Indian DCs; no green conditions
DPDP Rules (Nov 2025) | Soft localisation; RBI and SEBI rules drive local hosting more
Green Open Access Rules 2022 | 100 kW threshold; surcharges and banking still bite
IndiaAI Mission | Subsidised GPU compute bought from private operators

## Simulator
Simulator inputs (Reports 3–9)
4 tables. Source line under each title; "Note" gives the context sentence from the report.
SIM-T01 Simulator assumptions and evidence
Source: Atlas simulator (Reports 3–7)
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Simulator "Assumptions behind the simulator" table; feeds every simulator output.
Used to derive: Capex, cost per IT-kWh, energy, water, CO₂, MVA and incentives for any design.
Input | Value used | Evidence | Basis
Grid tariffs (energy + demand) | KA ₹6.70 + ₹365/kVA; MH ₹7.27 + ₹560; TN ₹7.50 + ₹608; TG ₹6.65 + ₹500 (FY2025–26 orders) | reported | State commission tariff orders, Report 7
UP and AP tariffs | ₹7.4 and ₹7.2/kWh (typical ₹7–8) | estimate | Not verified in Report 7
Renewable landed cost | ₹5.5–6.2/kWh open access; ≥₹6.4 for 90% hourly clean | estimate | SECI RTC ₹5.25 + charges; group captive ₹4.5–6.5 (Report 7)
Facility capex | Colo ₹56.1, hyperscale ₹39.2, AI ₹72.5 cr/MW before land; cooling adds ₹0–3 cr/MW | model | Report 7 cost stacks
GPU capex | ₹266 cr per MW of IT (~425 GB300-class GPUs/MW) | model | Report 7; GB300 rack price contested at US$3.7–6.5 m
Land | ₹3–20 cr per acre by city; 0.25–0.4 acre/MW | estimate | Report 7 and market reports
Cooling overhead and WUE | Function of design dry and wet bulb; towers ~1.8 L/kWh, adiabatic ~0.4, liquid + dry ~0.03 | model | Reports 3, 4 and 6
Grid carbon | 0.710 tCO₂/MWh for all states | reported | CEA v21; one national grid factor
Power-station water | Karnataka 1.5 L/kWh; other states 2.2 L/kWh | estimate | Reports 4–6
Water price | BWSSB ₹99/kL; ₹80 elsewhere; groundwater ₹20; treated + RO ₹40 | estimate | BWSSB tariff; others assumed
Electricity duty | 7.5% of the energy charge, where waived | estimate | Assumption; duty rates differ by state
Finance | WACC 11%; facility 20 years, GPUs 5 years | model | Report 7
Scarcity weights | Groundwater 1.0, municipal 0.7, treated 0.1, power stations 0.4, × city stress | model | Report 6; illustrative
SIM-T02 Simulator city parameters
Source: Atlas simulator (Reports 3–7)
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Simulator model inputs.
Used to derive: Capex, PUE, WUE and costs for each city and workload in the simulator.
City | State | Design DB (°C) | Design WB (°C) | Land (₹ cr/acre) | Grid energy (₹/kWh) | Demand (₹/kVA-month) | RE landed (₹/kWh) | Power-station water (L/kWh) | Water stress weight | Water price (₹/kL) | Coastal
Bengaluru | Karnataka | 35 | 23 | 8 | 6.7 | 365 | 6.2 | 1.5 | 1 | 99 | no
Mumbai | Maharashtra | 35 | 28 | 20 | 7.27 | 560 | 5.8 | 2.2 | 0.5 | 80 | yes
Chennai | Tamil Nadu | 38 | 29 | 6 | 7.5 | 608 | 5.9 | 2.2 | 0.9 | 80 | yes
Hyderabad | Telangana | 41 | 26 | 8 | 6.65 | 500 | 6.1 | 2.2 | 0.7 | 80 | no
Noida | Uttar Pradesh | 45 | 29 | 10 | 7.4 | 450 | 6 | 2.2 | 0.85 | 80 | no
Vizag | Andhra Pradesh | 36 | 28 | 3 | 7.2 | 475 | 5.5 | 2.2 | 0.6 | 80 | yes
SIM-T03 Simulator workload parameters
Source: Atlas simulator (Report 7)
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Simulator model inputs.
Used to derive: Capex, PUE, WUE and costs for each city and workload in the simulator.
Workload | Facility capex (₹ cr/MW, before land) | Acres per MW | Other opex (₹ cr/MW/yr) | Utilisation (%) | Power losses (PUE share) | Other (PUE share) | GPU capex (₹ cr/MW) | GPUs per MW
Colocation | 56.1 | 0.25 | 2.25 | 70 | 0.1 | 0.03 | — | —
Hyperscale cloud | 39.2 | 0.4 | 1.17 | 75 | 0.08 | 0.02 | — | —
AI training | 72.5 | 0.3 | 3.29 | 80 | 0.08 | 0.02 | 266 | 425
SIM-T04 State incentives modelled in the simulator
Source: State policies (Report 9)
Data basis: Source-derived (reported, not re-verified)
Used in atlas: Simulator incentive line and policy panel.
Used to derive: Incentive value per year and per IT-kWh.
State | ₹1/unit subsidy | Electricity duty waived | One-time bonus (₹ cr) | Note
Karnataka | no | yes | 20 | Electricity-duty exemption, plus ₹20 crore one-time for PUE ≤ 1.20 and reimbursements for WUE and treated water (Sustainable DC Policy 2026–31).
Maharashtra | yes | yes | — | ₹1/unit tariff subsidy and a 20-year duty waiver in green DC parks, conditional on at least 51% renewable power (GR, June 2026).
Tamil Nadu | no | no | — | The 2021 policy lapsed on 31 March 2026. No incentive applies until a successor is notified.
Telangana | no | no | — | A 2016 policy. Large projects get packages negotiated case by case, none of them published, so nothing is modelled here.
Uttar Pradesh | no | yes | — | 10-year electricity-duty waiver, plus a booster for PUE or green certification (DC Policy 2026).
Andhra Pradesh | no | no | — | Industrial tariff; transmission and wheeling relief case by case; stamp-duty and land concessions for mega projects (Policy 4.0).

## Key numbers
Key numbers (all reports)
1 tables. Source line under each title; "Note" gives the context sentence from the report.
KEY-T01 Key numbers cheat sheet
Source: Atlas Key numbers (all reports)
Data basis: Mixed: sourced figures plus estimates
Used in atlas: Key numbers cheat sheet (searchable list) at the end of the atlas.
Used to derive: Quick reference for the most-used figures; each row names its source.
Figure | Value | Source
Global DC electricity 2024 → 2030 | 415 → 945 TWh | IEA Energy and AI, Apr 2025
Global capacity 2025 → 2030 | ~103 → ~200 GW | JLL, Jan 2026
Hyperscale share of capacity | ~48% (→ 67% by 2031) | Synergy, Apr 2026
India operational capacity | 1,789 MW | Cushman & Wakefield, H1 2026
India pipeline to 2030 | 3,860 MW · US$29.9 bn | Cushman & Wakefield
Mumbai share of India capacity | ~50% (890 MW) | Cushman & Wakefield
Global average PUE | 1.54 | Uptime 2025
Google fleet PUE | 1.09 | Google, 2025
MeitY AI-cloud tender PUE | <1.35 | MeitY, since 2024
Indian leaders' PUE | 1.4–1.5 | SBI, Apr 2026
India grid emission factor | 0.710 tCO₂/MWh | CEA v21, FY25
Karnataka consumption mix | ~0.50 tCO₂/MWh | Series estimate
Evening fossil peak | ~174 GW at 7 pm | Ember, H1 2026
Coal lifecycle carbon | 820 g/kWh (India actual 900–1,100) | IPCC AR5
Indian coal water use | 2.8–4.0+ m³/MWh | CSE / CEA research
Karnataka grid water | ~1.5 L/kWh | Series estimate
Evaporation per kWh of heat | ~1.5 L | Latent heat 2,400 kJ/kg
50 MW evaporative withdrawal | 1.77 MLD (peak ~2.4) | Report 6 model
BWSSB delivered supply | ~1,935 MLD | Legislative Council, Aug 2026
Bangalore East groundwater stage | ~305% | 2024 assessment
Bengaluru DC water today | ~2–20 MLD (estimates) | DTE, IT dept, WELL Labs
100 MW AI campus energy | ~841 MU/yr · ~140 MVA | Report 4
Karnataka 1 GW target, evaporative | ~32 MLD | Report 4
Tier III build cost | ₹50–55 cr/MW (series model ₹56.1) | SBI / Report 7
AI / Tier IV build cost | up to ₹75 cr/MW | SBI, Apr 2026
Mumbai construction cost | US$6.64/W (51st of 52) | Turner & Townsend 2025
Colo LCOD (20 MW) | ₹29.7 per IT-kWh | Report 7
Mumbai colo rent, 1–5 MW | ₹6,500–8,000/kW/month | Cushman & Wakefield
H100 cost at 80% use | ~₹177/GPU-hour | Report 7
IndiaAI L1 rate (H100-class) | ₹150/GPU-hour | IndiaAI
IndiaAI GPUs | 38,231 across 14 providers | PIB, Mar 2026
SECI round-the-clock RE | ₹5.25–5.26/kWh | SECI tranche V, Aug 2026
Green 20 MW colo payback | ~2.3 years | Report 8
Green package abatement cost | ≈ −₹2,540/tCO₂ | Report 8
Karnataka PUE incentive | ₹20 cr for PUE 1.00–1.20 | Karnataka policy 2026–31
Karnataka policy outlay | ₹1,300.45 cr · 1 GW by 2031 | Karnataka, Sept 2026
HFC freeze in India | 1 Jan 2028 | Kigali Amendment
Liquid-cooling revenue | ~$3 bn (2025) → ~$7 bn (2029) | Dell'Oro, Jan 2026
GB200 / GB300 NVL72 rack | 120–150 kW | Nvidia / OEMs
Kyber rack (2027) | ~600 kW, 100% liquid, 800 VDC | Nvidia GTC
Budget tax holiday | to 31 Mar 2047 | Finance Act 2026
India subsea bandwidth via Mumbai | ~95% | Series sources